UPAMD Power states

201101101530

## Determining the load attached.

The need to determine the load that is attached to know what operations are available with that device type.

### Measure voltage on power pins prior to enabling safety voltage.  Voltage is present must be coming from another source.

### Supply 5V test voltage to CANH through 120 ohm resistor, and short CANL to Ground/Negative terminal.  Assumes device has 120ohm terminator. Assume dumb device has communications lines returned to negative terminal.

#### If VcanH = ~2.2V or higher – nothing attached

#### If VcanH = ~1.6V normal terminator for device

#### If VcanH = <0.5V – ground for dumb device.

## Device Class

Define major and minor device classes. 0-255 available, reserve 100 up for future versions of standard. Major class is second digit, sub-class is third digit.

### 000 – Undefined

Basic illegal state.

### 010 – Adapter/power source

Power provider

### 020 – Load device normal

### 030 – Bi-direction power flow

Can reverse power flow through negotiations based on priority.

### 031 – power storage

SubClass for large battery or other power storage devices that will draw power to charge and then provide power when needed.

### 040 – Intermittent power source – Solar, wind.

Intermittent power sources such as solar array.  Can be used to charge batteries and supply devices based on conditions.

## Priority

Nominal priorities are established by function.

Devices/Loads, users of power, are nominally allocated a priority of 150.  This priority can be changed based on internal circumstances within the device.

Adapters/Sources are nominally allocated a priority of 120. This priority can be changed based on needs within adapter/source.

Priority is used to modify current flow in both magnitude and direction in the system connected.

Priority can be asserted by a device to request a change in output voltage. It simply puts the load in the highest priority position at that time. Simply changing the priority to 100 will send to state 400 to determine action.

## Messages

| UPAMD Messages - 201101101530 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Message Type | Message | Data Byte 0 | Data Byte 1 | Data Byte 2 | Data Byte 3 | Data Byte 4 | Data Byte 5 | Data Byte 6 | Data Byte 7 |
| 0 | Heart Beat | Power priority Level | Request message | Heartbeat (24:31) | Heartbeat (16:23) | Heartbeat (8:15) | Heartbeat (0:7) | Standard Version UPAMD 2011 | Time from last heart beat in millisec (0..7) |
| 1 | Available power | Max Available Watts | Current Available Watts | Available power (Watt hours) MSB | Available power (Watt hours) LSB | Power priority Level | Maximum available Voltage 6bits volts 0-63, 2 bits 1/4V. | Device Class | Request message |
| 2 | Requested Power | Max Request Watts | Current Request Watts | Minimum Power | Minimum Volts | Power priority Level | Voltage Request | Device Class | Request message |
| 3 | Data Transfer Request up to 64KB | Total Byte count MSB | Total Byte Count LSB | Current position MSB | Current position LSB | Transfer data length 0-8 of odd transfer |  |  |  |
| 4 | Data Transfer | Data Byte 0 | Data Byte 1 | Data Byte 2 | Data Byte 3 | Data Byte 4 | Data Byte 5 | Data Byte 6 | Data Byte 7 |
| 5 | Vendor Identification | Vendor name byte 1 | Vendor name byte 2 | Vendor name byte 3 | Vendor name byte 4 | Vendor name byte 5 | Vendor name byte 6 | Vendor name byte 7 | Vendor name byte 8 |
| 6 | Model Number | Model byte 1 | Model byte 2 | Model byte 3 | Model byte 4 | Model byte 5 | Model byte 6 | Model byte 7 | Model byte 8 |
| 7 | Serial Number | Serial No byte 1 | Serial No byte 2 | Serial No byte 3 | Serial No byte 4 | Serial No byte 5 | Serial No byte 6 | Serial No byte 7 | Serial No byte 8 |
| 8 | EUI 8 octets | EUI-64 (56-63) | EUI-64 (48-55) | EUI-64 (40-47) | EUI-64 (32-39) | EUI-64 (24-31) | EUI-64 (16-23) | EUI-64 (8-15) | EUI-64 (0-7) |
| 9 | Manufacture Date YYYY:MM:DD:hh:mm:ss | Year most significant digits - Hex "Y" "Y" | Year least significant digits - Hex "Y" "Y" | Month digits - Hex "M" "M" | Day digits - Hex "D" "D" | Hours digits - Hex "h" "h" | Month digits - Hex "m" "m" | Seconds digits - Hex "s" "s" |  |
| 10 | Software Version | software Version byte 1 | software Version byte 2 | software Version byte 3 | software Version byte 4 | software Version byte 5 | software Version byte 6 | software Version byte 7 | software Version byte 8 |
| 11 | Firmware Version | Firmware version byte 1 | Firmware version byte 2 | Firmware version byte 3 | Firmware version byte 4 | Firmware version byte 5 | Firmware version byte 6 | Firmware version byte 7 | Firmware version byte 8 |
| 12 | Reservered for future use. |  |  |  |  |  |  |  |  |

# Power Adapter/Source:

Starting as an Adapter to power device(s).

## State 0 – Unpowered

Storage state, may have reserve power in batteries etc.

### Bulk, AC or DC, Power source connected

### Processor booted, Self check performed

### Go to State 1

## State 1 – Initial operation.

Safety test first to see if connected to another power source.

### Test for voltage on power pins

#### If voltage >3V -> State 300

Prepare for negotiations on function needed.

#### If voltage <3V -> State 4

Safe to look for attached devices.

## State 4 – Checking for attached device

Checking for basic connection to external device.  What type of device is attached.  Choice is NONE, Normal Communications capable device, and Dumb device that has no communication and is restricted to 20Watts, such a very small device or LED lighting or other such small devices.

This is unable to detect a device with a broken cable attached to the adapter.

### Temporarily apply 5V through 120ohm resistor to CANH, temproarily ground CANL

Apply a probe voltage to CANH through a disconnect transistor and a 120ohm resistor.

### Measure VCANH voltage

#### If VcanH = ~2.2V or higher – nothing attached

##### Set no communications lines attached Flag

##### Goto State4

#### If VcanH = ~1.6V normal terminator for device

##### Remove test probe voltage and CANL ground

##### Go to State 5

#### If VcanH = <0.5V –Communications lines grounded at dumb device.

##### Set Dumb Device Attached Flag

##### Go to State 100

## State 5 – Supplying Communications power

This state is only valid if a device with communications capabilities is available on the cable.  This state may be returned to for Standby or sleep mode with device still attached but not drawing any power.

### Set Current limit to 25ma

### Set output voltage to 12VDC (10-14V)

### Wait 1 second for device to startup

### Test for current usage

Perform a basic test of current usage by the device.  Possible test conditions are:  <5ma = nothing attached; >25ma is device short circuit; 10ma to 25ma = smart device attached.

#### If device current <5ma – nothing attached

##### Remove safety power

##### Go to state 1

#### If device current >25ma – device is shorted

##### Remove safety power

##### Go to State 1

#### If device current between 5 and 25ma

##### Set Device attached by power draw flag.

##### Go to State 6

## State 6 – Send Power Available message

Send Power Available message to device.  If standard device an ack will be received and power state defined.  If no ack received the device must be a dumb device or a broken communications link.  Attempt to deliver up to 20W of power to device. Message contains:

Max Available Watts (0-255 but limited to 130now)

Current Available Watts (if full power is not available)

Available power WattHours (0-65535 WattHours)

Current Capacity percentage (0-99)

Maximum available Voltage (6bit,2bit – 0-63V) reserved

Device Class

Device Priority (0-255) (120 nominal)

Message Request (message number)

### Wait for ACK

#### If NAK -> State 6

#### If ACK -> State 7

## State 7 – Wait for power requested message

The state will wait for and process the power requested message from the device. The message contains:

Maximum Requested Watts (0-255 limited to 130W now)

Current Requested Watts (0-255 limited to 130W now)

Minimum Power (0-255 limited to 130Wnow)

Power Priority Level (0-255)(150 Nominal)

Voltage Request (0-63V) Reserved

Minimum Volts (0-63V)

Device Class

Message Request (message number)

### If no message in 1 second -> State 6

### If power request  message received

#### Send ACK

#### Process message

##### If insufficient power available

###### Send NAC

###### Send Power available message

###### To -> State 6

#### If power available above Minimum -> State 8

## State 8 - Set Current limit and Output Voltage

State 8 does the power setup to meet the requested power or the power the port is capable of supplying.  If the request is from more than 20V control is transferred to state 400.

Input – from state 7

Output – either to state 400 or state 9.

### If voltage request not equal 20V -> Go to State 400

### Set output current limit to value

#### If Max Available > Max request -> max requested

#### If Max available < Max request -> max available

#### If voltage request =20V -> set to nominal (20V)

#### Enable Output power with ramp up

#### Go to State 9

## State 9 – Start heartbeat

State 9 initializes and transfer source  information to device and request device information as to vendor, model, serial number, EUI etc.

### Send heartbeat

### Send Id information

### Request ID information

### To State 10

## State 10 – Supplying power and monitoring requests

State 10 is the run state.  It will stay in this state until 1) changed by priority request, 2) changed by power management needs, 3) communication lines disconnected, 4) requested shutdown, 5) request for sleep mode or standby mode. While in this state the power is monitored and possibly tracked for reporting purposes.

### Monitor and measure current and power delivered

### Monitor Current levels to detect disconnect

#### If disconnect -> State 14

### Monitor Communication for failure – disconnect

#### If communications failure -> State 14

### Monitor device requests

#### If power change requested -> State 11

### Monitor adapter power needs

#### If adapter/source request power change -> State 12

### Loop in State 10

## State 11 – Changing Power output based on Device need

Changing power based on device request.

Input from state 10

Output to state 8 if power change is to be made

Output to state 10 if now power change is made

### Read power request from device

#### If requested power available

##### Send ACK and power available message

##### Go to State 8 to implement power change

#### If request is for 0 power – go to State 14

#### If request is for sleep mode – Go to State 13

### Set new current limit and voltage level if possible

### Return -> State 10

## State 12 – Change Power output based on Adapter need

This state is at the convenience of the adapter with permission of the device. The device is asked to accept a lower power, or higher power is available, and if accepted the power is changed accordingly, otherwise if device NAK, the change is refused and no change takes place. If request to device is for 0 power, the source is going down.

Input state 10 and internal need

Output to state 8 if change is to be made

Output to state 10 if no change.

### Send power available message to device

### Wait for ACK

### Read power request from device

#### If powers match -> State 8

#### If powers do not match ->State 10 with current power

## State 13 – Sleep Mode entry

Enter into a low power sleep mode by returning to startup safety voltage to keep device processor alive and communicating with heartbeats.

Input from State 11 request.

Output to state 8 if wakeup message

Output to state 14 on loss of heartbeat.

### Reduce voltage to safety voltage

### Reset current limit to 25ma

### Send and receive heartbeats

### If heartbeat message request power -> State 8

### If heartbeat stop -> state 14

### Go to State 13 – loop while in sleep mode.

## State 14 – Shutdown

### Remove all power

#### Return to State 1

# 20Watt low power: State 100 start

Got here by detecting <0.5V to ground on CANH line at device. This is to indicate a short to ground on one or both of the communication lines.

From State $

Function: supply up to 20W of power to load until communications pins are disconnected and voltage on VCANH rises above 0.5V.

Exit to State 14 - Shutdown

## Set output current limit to 1A

## Set output voltage to 20V

## State 101

### Monitor CANH voltage

#### If CANH voltage goes above 2.0v

##### Set current limit to 25ma

##### Remove Voltage to 0V.

##### Go to State 1.

#### While CANH Voltage <0.5v go to State 101

#### If VCANH  >0.5V goto State 13

# Device/Sink:  State 200 start

Entry from communications power be applied to sink device

Entry from change is power direction from state 300

Function – start the use of power by the device/load. This assumes device has communications capability. Determine if the minimum power for this device is available, if not send NAK and indicate bad power through LED etc.

## Send power request message to source

### If ACK

#### Goto State 201

### If NAK

#### resend power request message

#### goto State 200

# State 201 – Determine if enough power is available

Receive power available message from source.  Determine if power available is sufficient for minimum operation of the device. If yes device determines the use of the available power and enables that power.  If no device sends message with minimum required power and notifies user of insufficient power.

## Wait for power available message from source

## Send ACK

## If power > minimum power

### Resend power request to confirm power.

### When voltage raises to requested voltage

#### Enable power converters

#### Send heart beat

#### Monitor priority and power available messages.

##### If change in priority

###### If my priority > source priority

Continue

###### If my priority < source priority

Request available power message

Determine response to changed request

Adjust usage model if possible

Continue if ok

Start shutdown if not possible

If power requested from sink

If not capable signal NAK

If capable Go to state 2

#### If device requests disconnect

##### Send power request of 0 to source

##### Stop power usage

##### Stay on safety power through disconnect

#### If device requests more power

##### Send updated power request to source

###### If power available message matches request

Make use of increased power

#### If power available message lower then current

##### Test against minimum

###### If less than minimum send NAK

###### If greater than minimum send ACK and adjust.

###### Go to state 201

#### If device requests sleep

##### Request 0 power

##### Shutdown converters

##### Maintain heart beat

##### Goto state 200

#### Remain in state 201

## If power < minimum power

### Send NAK

### Send requested power message

### Goto state 200

# Bidirectional Power Source/Sink: State 300 start

Entry from: Got here either by having communication, or more, voltage applied to power pins initially or through a change in priority.

Function: If priority of connected note greater than this node, assume role requested of the higher priority node, if possible, or return NAK to request to refuse service that cannot be provided.

## Send power available message with priority

## Wait for ACK

### If no ACK goto state 1

### If ACK

#### Read power message and check priority

##### IF received priority > internal priority

###### If power request message and have capability

Assume roll of device Class 010 power provider

Send power available

###### If power available message

Decide on accepting roll of Class 020 load to fill internal battery or to add to power into hub.

Goto state 200

##### If received priority < internal priority

###### Send NAK

###### Go to state 1.

# Higher power: State 400 start

Got here from request for other than 20.0Volts at State 8

This function is to allow higher power to the load if the source is capable of it. If the source is not capable, a simple NAK is returned to the requester and continue with the current allocation.   If higher power is available from the source the request will be affirmed with an ACK and the higher voltage applied and current limit set.

Exit is to state 7 if the higher power is not available

Exit is to state 8 if the power is available.

## Send available power message

## Wait for ACK

### If no ACK go to State 6

## Read Power Request message

### If power available is as requested

#### Send ACK

#### Go to State 8

### If power requested is not available

#### Send NAK

#### Send power available message

#### Goto state 7

### Else go to state 1