## Unapproved SCIF F13 Minutes v1

## SC Insulating Fluids Meeting

October 23, 2013

St. Louis, Missouri

## Insulating Fluids Subcommittee: 
Chair Susan McNelly
Vice-Chair Jerry Murphy
Secretary C. Patrick  McShane

### Introductions, Roll Call, Meeting Approvals, and Chair’s Comments

### Introductions by all attendees

### Chair’s comment: The Chair gave a summary on the groups need to follow the Code of Ethics as well as a reminder of WG/TF meeting requirements.  Among these were: a count of any motions not unanimous must be provided including a count of negatives, a 2/3 vote is needed for a WG to approve a change of WG scope, as well as to move a draft project to the Sponsor SC for approval to go to ballot. Attendance of WG and TF meetings must be kept in the AM System. She indicated that the attendance does not need to be listed in the actual minutes as long as the AM System is used as required.

### Roll Call of SC members.

### Roll Call of eligible new members. Three were present and the Chair welcomed them as new members:

- Josh Herz

- Rowland James

- Min Jea Lee

There were 25 SC members and 53 guests in attendance at the meeting.  A quorum was achieved.  The following guests requested membership in the IFSC:

Shawn Galbraith

Tom Golner

Roger Hayes

Poorvi Patel

Jose Izquierdo

Zam Kiparizoski

Egon Kirchenmayer

### Agenda Approval

### Motioned by: Jim Graham

### Seconded by: Claude Beauchemin

- SC Vote Outcome: Passed unanimously

### Corrections and Approval of minutes from fall 2012, Milwaukee

### Motioned by:  Don Cherry

### Seconded by: Claude Beauchemin

### SC Vote Outcome: Passed Unanimously

### Corrections and Approval of minutes from spring 2013, Munich

### Motioned by: Clair Claiborne

### Seconded by: Don Cherry

### Outcome: Passed unanimously

### WG & TF Reports Presented at the SC Meeting

#### C57.104 – IEEE Guide for the Interpretation of Gases Generated in Oil – Immersed Transformerseting WG Chair Rick Ladroga, Vice-Chair Claude Beauchemin

The WG Report at the Sub-Committee Meeting: Presented by Sue McNelly:

The vice-chair gave an informative presentation on Data Analysis: The Rate of Change.

An ambitious schedule was presented to the WG to finalize the data and have a draft of the document out for review by December, a WG Ballot by the end of January, and a Sponsor ballot by April of next year as the PAR expires the end of 2014.

The Minutes (unapproved) of C57.104 WG Meeting as Submitted:

The meeting was called to order by Chair Rick Ladroga on Tuesday, October 22, 2013 at 3:15pm.  Vice Chair Claude Beauchemin and Secretary Susan McNelly (writer of Minutes) were also present.

There were 52 of 81 members present.  There were 64 guests, and 7 guests requesting membership.  A membership quorum was achieved.  Guests attending the WG meeting for the first time who request membership will be deferred until the next meeting attended.

The following guests requesting membership were (those identified with an asterisk (4 of the 7) will be added as WG members):

Gustavo Acero	Richard Simonelli *

Jeffrey Golarz *	Rogerio Verdolin

Paul Griffin *	Peter Zhao

Emilio Morales-Cruz *

Agenda

1.	Welcome & Introductions

2.	Quorum Check

3.	Approval of Minutes from Fall 2012 Milwaukee meeting and Spring 2013 Munich meeting.

4.	Chair’s Remarks

5.	Presentations

a.	Data - Claude Beauchemin – Full presentation was not completed

b.	Case Studies – Paul Boman – Time expired before this could be presented.

6.	Adjourn

Introductions and member roll call were performed.  A quorum was achieved.

Motion to approve the Fall 2012 Milwaukee, Wisconsin meeting minutes was made by Don Cherry and seconded by Tom Prevost.  The motion was unanimously approved.

Motion to approve the Spring 2013 Munich, Germany meeting minutes was made by Jerry Murphy and seconded by Tom Prevost.  The motion was unanimously approved.

Chair’s Remarks:

The chair indicated that the group has been meeting both at the Transformer Committee Meetings and at least a couple of additional times per year.  There is a lot of data involved that has tremendous commercial value.

TFs:

Framework:  Jim Dukarm, Dave Hanson, Rick Ladroga

Data: Norm Field, Luiz Cheim, Claude Beauchemin

Diagnostic Methods: Michel Duval, Dave Wallach

Case Studies: Paul Boman, Arturo Nunez

Arc Furnace TRs: Tom Lundquist

Bibliography: Jerry Murphy, Tom Prevost

Tom Prevost gave a summary of the progress on the data storage and access issue.  There are three other groups that are dealing with the same issue.  IEEE will provide a data suppository and there will be a non-disclosure document created to help provide assurances that the data will not be misused for commercial gain.  The expectation is that this will be in place by the next meeting in Savannah.

Case Studies: presented by Paul Boman

Paul indicated that they are attempting to display the information in the easiest to read format.  Diagnostic techniques, gas profiles from sample-to-sample, rates of change, confirmation samples, and diagnosis (when possible) will be part of the case study examples.  There are approximately 25 case study examples.

Data: Rate of Change, presented by Claude Beauchemin

Change in PPM, PPM/day, PPM/year, what makes sense?

At the fall 2012 meeting Luiz Cheim presented on this topic.  This presentation is on the web.  This presentation also covered the various aspects of rate comparison.

Claude indicated that from Luiz’s presentation it was shown that the shorter the period, the higher the value of rate of gas increase.  Because of this, further analysis was done on approximately 123,000 DGA samples on approximately 44,000 transformers.

The first thing looked at was the sampling interval.  There was one very large peak at 1 year (57% of data).  Therefore the bulk of the data was based on a yearly sampling interval.  With a much smaller peak at 6 months (11%).

Looking at the trends from this data: One question that needs to be asked is what “noise” or DGA variation is resulting from oil sampling, transport, and analysis differences from one sample to the next.

Claude indicated that if we want to use a PPM/year or PPM/day, then a method to handle the spread is needed.

If instead the absolute difference is used, the ratio is reduced by a factor of 100, which makes it much more manageable.

Questions: The following is a portion of the questions/discussion that followed the presentation.

Fredi Jacob – Is there some built in bias?  His overall reaction is that maybe the PPM/day is dependent on the interval between the samples and should only be used if you have decided the gassing is high and you have a problem.

Claude responded that the work is not quite finished.

Shuzhen Xu – Suggested that to remove the noise, first you average the data.

Tom Prevost – Indicated that it costs money to sample, so most people are not going to sample unless there is a suspected problem.  He suggested that the graphs in the document need to be fairly uncomplicated.  He recommended that the one year data be used in the guide.

Don Platts – Indicated that the analysis is not practical for the normal user of the guide.  They will be looking for guidance on what rate of change is acceptable and what action they should take based on the rate of change.

General

Rick indicated that the goal was to obtain real data.  The challenge now is to boil this tremendous amount of data down into tables that can be used by the users.

To stay on track with the document, Rick indicated that he would like to have the following schedule in line with a December 2014 PAR expiration date:

- Complete data collection by November 1

- Meeting November 4 or 5 to finalize analysis of data

- Draft to the WG by November 28

- Discuss comments on draft by January 7

- Issue a WG ballot by January 28

- Resolve WG ballot comments by March 2014

- Issue V2 for ballot April 15, 2014

- Discuss ballot negatives

- Resolve comments May – June 2014

- Recirculation Ballot

The meeting was adjourned at 4:35 pm.

Rick Ladroga

WG Chair

Claude Beauchemin

WG Vice-Chair

Susan McNelly

WG Secretary

#### C57.106 – IEEE Guide for Acceptance and Maintenance of Insulating Oil in Equipment

WG Chair Bob Rasor, Vice-Chair Jim Thompson, Secretary Claude Beauchemin

The WG Report at the Sub-Committee Meeting: Presented by Bob Rasor:

There were several phone conferences over the summer to review specific sections of the guide with the TF leaders. Some progress has been made, but the need of a more efficient process was recognized.  Major revisions to the Guide are not expected to be needed.  One issue is whether or not  the standard should include mineral oil used in circuit breakers. A liaison with the Switchgear Committee will be assigned. The WG is looking for some additional TF leaders.

A revision of the acid number in Table 1 and 2 will probably be needed. ASTM analytical method is reported has having a reproducibility of 0.015, which is the maximum value given in Table 1 and 2 of the Guide.

The Minutes (unapproved) of C57.106 WG Meeting as Submitted:

Fall Meeting 2013, St-Louis Missouri, October 21, 2013. 16H45

Attendees:  62 (including 2 proxy). Members: 18 out of 33: Quorum is obtained

New Membership request: 4

Jeff Golauz (or Golavz), Paul Griffin, Richard Simonelli, Ryan Thompson

Adoption of Fall 2012 and Spring 2013 minutes.

Review of past year activities:

No quorum in Germany meeting.

There were several phone conferences over the summer to review specific section of the guide with the TF leaders. Some progress was done, but the need of a more efficient process was recognised.

It was proposed to divide up the work to several TF, each assigned to TF chair as follow:

Acknowledgements and bibliography:			(need TF lead)

New transformer tables:				(Hali M.)

Thermodynamic Moisture Equilibrium:		(Dave H.)

ASTM and definitions:				(Clair C.)

Breakers						(need TF lead)

LTCs						(need TF lead)

Environmental  					(Stephanie D.)

A request for TF volunteers to fill the vacant TF chair will be posted and emailed to active members.

Review of documents done to date:

Several editorial changes have been applied during the summer conference call.

A revision of acid number in table 1 and 2 is probably needed. ASTM analytical method is reported has having a reproducibility of 0.015, which is the same value as in table 1 and 2. However, a standard limit should not be set equal to a method reproducibility limit, as the method could then not supply the required precision to guarantee the standard requirement.

The actual ASTM D974 method reproducibility limit will be verified and the guide will be adjusted accordingly.

Section 8 on breaker raised two discussions:

1- A reference in section 8.1 to the effect that adding inhibitor could affect thermal characteristic of oil would be removed as this statement is inaccurate.

2- The pertinence of the inclusion of a section (section 8) on oil breaker in a Transformer guide is also debatable, as this might be better covered by the Switchgear committee. If it turn out that it is required, then a confirmation for the pertinence of this inclusion in a transformer guide will need to be reaffirmed between the transformer committee and the switchgear committee. To be followed up.

Meeting was adjourned at 18H00

#### WG C57.121 – IEEE Guide for Acceptance and Maintenance of Less-Flammable Hydrocarbon Fluid in Transformers

#### Chair: David Sundin

The WG Report at the Sub-Committee Meeting: Presented by David Sundin

The WG amendment for C57.121 had its initial meeting on Tuesday. 40 attended, 7 requested membership. There was a quorum. This WG is making the first revision of the original standard guide published in 1988.  There was discussion on whether  there is a need to change IFT value based on commercially available insulating fluids. Does this value need to be included?  Paul Griffin stated that he recommended any change be communicated to ASTM, WG headed by Jimmy Rascoe.

The Minutes (unapproved) of C57.130 WG Meeting as Submitted:

Working Group on Amendment of C57.121, IEEE Guide for Acceptance and Maintenance of Less Flammable Hydrocarbon Fluids" had its initial meeting at 1:30 pm CST in St. Louis, MO

The WG was chaired by David Sundin

There were 40 in attendance, of whom 7 requested membership.

The WG Chair acted as secretary.

The chair explained the scope of the WG being a revision of the Guide that would change the Interfacial Tension value to reflect oils that are commercially available.   Specifically, the minimum IFT value recommended in the Guide is 40 mN/m2, and the chair, representing the only North American manufacturer of the fluid, recommended a value of 30. There was some discussion with regard to the utility of a value of 30, and whether the Guide should follow the example of the Natural Ester guide and simply not include a value for IFT.

Paul Griffin noted that ASTM D5222, Specification for High Fire Point Electrical Insulating Oils, contained a minimum value of 40 mN/m2 for IFT, and that traditionally, IEEE accepted the values of ASTM specifications in cases such as this, and that he recommended that this precedent be followed.  There was more discussion regarding whether there exists justification for a value of 30 mN/m2, and if so, whether it should be presented to ASTM, which is currently reaffirming ASTM D5222 specification.  Jimmy Rasco stated that he was spearheading the effort at ASTM D27 to reaffirm this Standard Specification.

Roger Wicks asked whether other changes to the Guide would be undertaken at the next revision and was assured that they would, but that the next revision is currently scheduled for 2019.

There was a discussion with regard to the historical difficulty that High Molecular Weight Hydrocarbon fluids had in maintaining an IFT value of 40 mN/m2.  David Sundin commented that this value was set artificially high during the first version of C57.121 in 1988 by commercial competitors as a means to discredit this type of oil, as the commercially available oils would have difficulty in meeting this value.

Don Cherry made a motion that "David Sundin will present data to ASTM Committee D27 that will support a revision  of ASTM D5222 to include a minimum acceptance value of 30 mN/m2, and that the WG would then amend C57.121to match that value".  The motion was seconded by Paul Griffin and was passed with unanimous support by all attendees who had indicated an interest in being members of the WG.

There being no other business to attend, the chair asked for a motion of adjournment.   Don Cherry made that motion, which was seconded by Clair Claiborne, and passed unanimously.

Respectfully submitted,

David Sundin

#### WG C57.130 - IEEE Guide for Dissolved Gas Analysis During Factory Temperature Rise Tests

Jim Thompson– Chair, Tom Prevost- Vice-Chair

The WG Report at the Sub-Committee Meeting: Presented by Jim Thompson

A PAR revision has been requested to remove the “Trial-Use” language from the Guide’s title. The WG is also requesting to add the word “mineral” before “oil”.

The current draft has DGA volume limits lower than three other documents including the IEC standard.

The Chair will make the WG Ballot comments available for review within the next two weeks.  The comments will be posted on the web. The intent is to have a revised draft available for ballot early next year, however, there is significant work needed to come to a consensus on Table limits.

The Minutes (unapproved) of C57.130 WG Meeting as Submitted:

October 22, 2013

Unapproved Minutes Working Group Meeting for IEEE PC57.130

IEEE “Guide for the Use of Dissolved Gas Analysis Applied to Factory Temperature Rise Tests for the Evaluation of Mineral Oil-Immersed Transformers and Reactors”

Chair Jim Thompson

The working group meeting was conducted on October 22, 2013 at St. Louis, Missouri with 85 people in attendance, including 9 of the 14 current working group members.

This document was in draft 18 when the decision was made to let the PAR expire in 2009.  A new PAR was approved on June 17, 2010 and is presently in draft 3.

The previous minutes from F12 (fall 2012) were presented for approval.  The F12 minutes approval, motion by Vijayan and second by Don Platts, was followed by unanimous approval.

A previous unanimous motion at the F11 meeting to change the guide from a trial use guide to that of a guide and to add the word “mineral” to “oil” in the title has been carried forward to the SA in the form of a PAR amendment.  These changes were recently submitted to IEEE Standards Association Standards Board New Standards Committee for approval.

The meeting discussion included straw ballot comments regarding table 1 “Gas Generation Rate Guidelines.” The chair presented data for four data sets with gas generation rates in a power point presentation.  Also guideline gas generation rate limits were presented in table form from two IEC documents, along with suggested rate limits from the document reference B6, Oommen (1982), and the rate limits presently in the draft document.  It was noted by the chair that in general rate limits were much higher than in the current document table 1.

It was also noted by the chair that several of the data sets submitted to the working group have data points greater than the current document rate limits for level 1.  Level 1 has a description of “no problem detected”.  The chair noted that the data indicates that a significant percent of the transformers from the data showed was gassing over the rate limits in the draft document.  It was suggested that the rates be increased slightly for hydrogen and carbon dioxide according to the Oommen values.  The chair asked for discussion.

The discussion included one wg member suggesting the limits should be lower for HC (methane, ethane, and ethylene).  On the other hand 5 people in attendance suggested the limits should be higher for HC, carbon monoxide, and hydrogen. There was a question as to where this data came from.  The chair noted that the data source was requested to be anonymous.  A comment was made that the gas generation rate will be influenced by voltage class, size, construction (core or shell) and paper/oil ratio.

A motion, presented to the wg members by Tom Prevost, seconded by Vijayan, in the audience, to accept the limits as-is: failed to pass.  Another motion by Tom Prevost, seconded by Vijayan, presented to the wg members in the audience, to keep the limits as-is but to lower the limit for HC to 0.2, 0.5, and >0.5 ppm per hour in table 1: failed to pass.

On another issue, Juan Castellanos suggested that the document might apply only to 10 MVA and greater transformers with a voltage rating of 69KV or higher.  The chair noted that the straw ballot response will be completed taking into account the discussions of the meeting.  After that the document will proceed towards a ballot.

Respectfully submitted,

Chair Jim Allen Thompson

#### IEEE C57.139 IEEE Dissolved Gas Analysis in Load Tap Changers

WG Chair David Wallach, Secretary Sue McNelly

The WG Report at the Sub-Committee Meeting: Presented by David Wallach:

A second draft of the document has been posted on the WG web page and is also available on the Central Desktop site.  Dave expressed special appreciation to Michel Duval, Jim Dukarm, Rainer Frotscher, and Fredi Jacob for their work on the draft since the last meeting.  The plan is to have a WG Ballot issued before the Spring 2014 meeting in Savannah.

The Minutes (unapproved) of C57.139 WG Meeting as Submitted:

Chair Dave Wallach called the WG meeting to order on Tuesday, October 22, 2013 at 11:00 am.  Vice-Chair Mark Cheatham and Secretary Susan McNelly (minutes written by) were also present.  There were 32 of 63 members present (Quorum requirement was met).  There were 62 guests present with 3 guests requesting membership.  Guests attending the WG meeting for the first time who request membership will be deferred until the next meeting attended. The membership roster and attendance will be recorded in the Committee AM System.

The following guests requested membership in the WG and will be added as members:

Rainer Frotscher

Jeffrey Golarz

Richard Simonelli

Agenda:

1.	Introductions/Member Roll Call

2.	Approval of minutes from Fall 2012 and Spring 2013 meetings

3.	Document Status

4.	Old Business

5.	New Business

6.	Adjourn

Introductions and member roll call were performed.  A quorum was achieved.

Motion to approve the Fall 2012 Milwaukee, Wisconsin meeting minutes was made by Bob Kinner and seconded by Mark Perkins.  The motion was unanimously approved.

Motion to approve the Spring 2013 Munich, Germany meeting minutes was made by Craig Colopy and seconded by Brian Penny.  The motion was unanimously approved.

Document Status

Dave Wallach gave the following status update:

The WG is using the Central Desktop where a working draft of the Guide is available for review and comment.  He indicated a special appreciation to Michel Duval, Jim Dukarm, Rainer Frotscher, and Fredi Jacob for their work since the last meeting.

Dave indicated that he would like to send out the draft for a WG ballot before the Spring 2014 meeting in Savannah and would like to have a vote at that meeting to send the document through for Ballot by mid 2014.

Dave asked if there were any updates to the spreadsheet out on the street.  No comments were made.

Section 5.3.3 Resistive Tap Changers has undergone considerable revision.  Rainer Frotscher discussed the revisions made to this section.  An attendee expressed concern over a portion of the revised text. There will be some additional offline discussion required to modify the content of this section.

Michel Duval indicated that there has been a lot of discussion regarding the presence of acetylene from low arc energy in a small amount of oil.  Mike Lau shared his experiences that over time, they have seen a switch to pattern B.  Michel indicated it could be due to a high current flowing through contacts due to coking.  Fredi Jacob asked if there had been any tracking of the current due to coking.  Rainer indicated that it is due to different switching speeds.  Luiz Cheim suggested the recovery voltage arc resistance be measured.

Dave urged the WG members to review the latest document and provide comments.  He would like to get this out for a WG ballot prior to the Spring 2014 meeting in Savannah.

Old Business

No old business was discussed.

New Business

No new business was raised for discussion.

A motion to adjourn was made by Claude Beauchemin and was seconded.  The motion was unanimously approved. The meeting was adjourned at 11:45 am.

Dave Wallach

Chair

Mark Cheatham

Vice-Chair

Susan McNelly

Secretary

#### IEEE C57.147 Guide for Acceptance and Maintenance of Natural Ester Fluids in Transformers

WG Chair: Patrick McShane, Vice-Chair: Clair Claiborne, Secretary: Jim Graham

The WG Report at the Sub-Committee Meeting: Presented by Patrick McShane:

An update on IEC 62770, Unused Natural Esters for Transformers and Similar Equipment was presented by Clair Claiborne.

Rainer Frotscher presented a proposed Annex C on Natural Esters for LTCs.

If the outstanding TF assignments are not completed by Feb. 15, the WG officers will review assigned sections and edit as needed in current Guide.

The Minutes (unapproved) of C57.147 WG Meeting as Submitted:

WG C57.147, October 21, 2013, St. Louis, MO

•	Call to Order was made at 3:15 PM.

•	Introductions/Membership Attendance/Quorum Check

•	Attendance:  23 of 36 members present, quorum was achieved. 33 guests. Total: 56

6 guests requested membership.

•	A motion to approve the Spring 2013 minutes was made by Don Cherry, seconded by Jerry  Murphy.  The Spring 2013 Minutes were unanimously approved.

•	Chair's Remarks, Patrick McShane:

- Welcome of new members

- Discussion of a new task force established by the Insulating Fluids Subcommittee for the consolidation of the insulating liquids maintenance guides, including C57.147.

- Review of the time line goals for completion of the guide revisions:

1.	All outstanding TF assignments will be dealt with asap

2.	If TF assignments are not completed by Feb. 15, the WG officers will review assigned sections and edit as needed in current Guide.

3.	First draft to be reviewed at S15

4.	To assist in insulating liquids guide consolidations project, the SA approval target is Q3, 2015; 5 quarters prior to PAR deadline.

•	Clair Claiborne presented an update on IEC 62770, Unused Natural Esters for Transformers and Similar Electrical Equipment.  Clair highlighted differences between IEC document and its equivalent, ASTM D6871.  IEC added an oxidation stabilization test, but this was controversial.  The FDIS was issued August 2013, and voting terminated 18 October, 2013.   The international standard will be published before the end of this year.  Discussion included questioning of why the IEC dissipation factor is higher, 5% vs. IEEE 4%. A: Apparently to include all available products available. Rainer Frotcher stated he does not agree with the 28 hour duration for the oxidation test. A: The goal of the TC was not to repeat what happen in their standard for less-flammable insulating liquids which kept some commercially available products from the IEC market.

•	Rainer Frotscher presented a proposed Annex C titled Natural Esters for Load Tap Changers (LTCs).  This will be posted with the minutes for working group review.

•	Task Force Reports:

- Stephanie Denzer reported via email TF8 had met since the Spring 2013 meeting and submitted a revised draft of section 8. This will be posted on the web site for working group review.

- David Sundin presented a current draft of Annex B, titled Additional technical information.  There was additional discussion regarding the removal of the 300C minimum fire point limit from Table B.5 and Table 5 in the main document.

- The drafts received will be made available to the working group to review.

•	Old Business:

- TF chairs will be notified their final reports are due February, 2013 so the working group can review their work prior to the Spring 2014 meeting.

- WG officers will review the C57.93 installation guide to determine if any of the items of interest for revision would be more appropriately addressed in the installation guide.

•	New Business:

- Roberto Asano made a motion to remove the fire point properties from Table 5 and move this information elsewhere within the guide.  Don Cherry seconded the motion.  After spirited debate, a motion was made by Jim Graham to close discussion, seconded by Don Cherry.  The motion to close discussion carried, and Mr. Asano’s motion also carried.

•	The meeting adjourned by acclimation at 4:30 pm.

Respectively submitted, Jim Graham, WG Secretary

#### PC57.155 – Guide for Interpretation of Gases Generated in Natural Ester and Synthetic Ester Immersed Transformers

Chair Paul Boman, Secretary John Luksich

The WG Report at the Sub-Committee Meeting: Presented by Paul Boman:

Results from the initial Draft 4 sponsor ballot was reported to Working Group:

Ballot Closed: 17-Oct-2013 with 90 comments (6 negative ballots), 37 of which must be satisfied.

The ballot has met the 75% returned ballot requirement.

Ballot resolution work has begun.  There were five items that were difficult to resolve:

- Ostwald Coefficients appear to be laboratory dependant and the annex will be removed.

- Section 4 that covers DGA theory was deemed too overwhelming, so the section will be summarized and moved to the Appendix.

- Recognized need to get more DGA data to substantiate the limits recommendations.

- A concern was raised that the user may not know which insulating liquid is being tested, but the comment was rejected unanimously by the resolution TF.

- Agreed to removed two tables of the Ostwald Coefficients lab results while adding additional guidance of the tables.

It has been decided that publishing the document as an IEEE/IEC dual logo document will not be pursued at this time. Draft 5 with comments will be on the web site. There will be a new ballot. Sue McNelly stated that since the document is already in the balloting stage, the approval to recirculate for a new ballot does not need to be voted by the full IF Subcommittee.

The Minutes (unapproved) of C57.155 WG Meeting as Submitted:

PC57-155 Guide for Interpretation of Gases Generated in Natural Ester and Synthetic Ester Immersed Transformers

Report given at the Sub-Committee Meeting: WG meeting minutes (unapproved) as received:

Paul Boman– Chair,   Patrick McShane – Acting Secretary

Meeting Date:  October 22, 2013	Time:  9:30 AM

Attendance:  16 members of 26 members including 4 corresponding members were in attendance and the total attendance was 95.

- Introductions

- Quorum present

- Approval of Meeting Agenda

- Approval of Meeting Minutes for Fall 2012, Claude Beauchemin motion and Don Cherry 2nd motion, Working group approved unanimously

- Approval of Meeting Minutes for Spring 2013 Claude Beauchemin motion and Don Cherry 2nd motion, Working group approved unanimously

Continued business

-Initial sponsor ballot information was reported to Working Group:

Ballot Open Date: 17-Sep-2013

Ballot Close Date: 17-Oct-2013

Type: New

Draft #: 4

Comments: 90

Must Be Satisfied Comments: 37

RESPONSE RATE

This ballot has met the 75% returned ballot requirement.

96 eligible people in this ballot group.

69 affirmative votes

6 negative votes with comments

0 negative votes without comments

4 abstention votes: (Lack of expertise: 3, Other: 1)

79 votes received = 82% returned  5% abstention

APPROVAL RATE

The 75% affirmation requirement is being met.  69 affirmative votes  6 negative votes with comments

- Draft guide 4 comment resolution

- Most comments made to Draft 5

- Draft 5 and comments will be placed on Transformer Committee web site for Working Group

- Ballot Comment Resolution Items

- Item 1:

Comment #	Page	Sub-clause 	Line

i-28, matrix sheet 2 	37	F	3

Annex F - What is the origin of this data?  Should that not be noted? And Sheet 2 Comment Table F.1 contains erroneous data

There needs to be some narrative explaining the information contained in this annex.  Also it should be pointed out that Synthetic Ester B is measured at a different temperature than the other fluids.

Concerned that the Synthetic Fluid B had a different reference temperature at 20º C and the table needed references.

Overriding concern is the comment about erroneous data.

Clair Claiborne, some problems in developing the OC for high oleic, and other esters.

Don Cherry, “I question why data needed in the guide?”

Mel Gel: Not to be used for analysis (ASTM uses), the data is useful to lab to discuss with clients tell you how solubility, explaining why results change, the why.

Michel Duval: Data helps if have nitrogen blanket with partition coefficients.

George Frimpong: we know some of these numbers are wrong.

Luis Cheim: Maybe indicate only as reference.

Valery: 20 C for different liquid.

Motion on  item.1: Don Chu Remove Table F.1 from document Don Cherry 2nd motion

Discussion Fred Jakob: run per std (ASTM? ANSI? )Std 3612C . Most labs will use their own run of OC.

Working Group Vote Yes 13, No 1 Motion Passed

Comment #	Page	Sub-clause 	Line

i-14, i-51 		Section 4

Acid production -Figures 7 thru 17 (lines 1-23 & 7-18)

Move chemical reaction figures to an Annex (as a chemist I can see and understand the figures depicting the chemical reactions showing the formation of specific gasses.  I believe that the everyday user may not find this as useful.  They are interested only in the resulting gasses).

Chair: Several comments to take Section 4 remove from main body and make it an annex.

Don Cherry made motion to move bulk of Section 4 to informative annex , Jerry Murphy seconded motion.

Working group approved unanimously and Motion passed

Chair formed TF: Dave Hanson chair TF, Jerry Murphy, Claude Beauchemin and Don Cherry.  Shorten theory section, put rest in informative annex.

Comment #	Page	Sub-clause 	Line

i-32, i-61, i-36 		6

The scope and purpose of this guide is listed below.  While the draft document does a good job of providing both the theory and bibliographic references, I feel that the guidance given for interpretation and recommended actions is lacking.  If I was a user with the results of a DGA in my hands it would be a real struggle for me to determine whether the reported results are good or bad.  Likewise if the results are bad what is the recommended action that should be taken?  I understand that this is a new area and that there is limited data available.  However, our charge should be to provide clear guidance to the user.  I do not see where this document in its present form meets that goal.

Comments on Mostly Section 6: Concern of lack of guidance on interpretation and actions as required by Scope Item 3. Chair wants it done right, not rushed.

Chair asked if Working Group wants to address this item, no answer.  Chair commented on Section 6 revises that included Table 1 and Figure 1 draft then discussed with copies of Section 6 handed out for the discussion. The general feeling from the negative balloters in the group (Don Cherry and Clair Claiborne) and the Working Group that this is the correct direction. One of the negative balloters was not present at the Working Group meeting and no feedback has been received yet.

Don Cherry need to quantify condition 1 ,2, 3. Like c57.104 if possible or remove.

Section 6 is of most concern to Chair.  Any changes now are limited to sections that deal with comments. Comment received that need to address other sources of gases that are not related to stray or fault gases. Fuse, rectifier transformer or load-break switch so a note was placed into Section 6.

Comment #	Page	Sub-clause 	Line

i-60 	1	1.1	19

The proposed document does not have a direct interpretation of the gas results for these fluids.  The % in table 1 are only useful if one knows the fluid in the equipment and if the users orders fluid according to ASTM D6871 there is no way that a user is able to determine what fluid may be in equipment.  The % are so diverse no conclusion may be drawn from the data.  This document is probably a white paper not a guide for interpretation as there is none in the main document that is useful.

Comment: Chair presented Ballot Comment i-60 as item 4. Comment i-60 states experimental data and Table 1 information inadequate for a guide, this should be a white paper not a guide. Objection is users will not know which type of fluid is being used and which information to use. The i-60 balloter name was not given to Working Group and he did not attend the Fall 2013 meeting.

Threshold was explained and the usage reference from C57-146 DGA Guide for Silicone Fluid

Jerry Murphy: Motion to reject comment i-60, Don Cherry 2nd Motion

Jerry Murphy we need a guide and supports Guide in current forms including Section 6. General group feeling is that Section 1.3 gives limitations that user needs to know details about the equipment.

Working group approved unanimously and Motion passed

Comment #	Page	Sub-clause 	Line

Sheet 2 	16 through 18	Table B.1 and C1

Why do we even have this in this document?  Would this not be better in ASTM D6871?

Needs some wording on the reason for this type of testing.  Used for mineral oils to demonstrate a particular phenomenon associated therewith.

Comment that Table B.2 – ASTM 7150. Chair thought germane to topic and data available. Michel Duval thinks very import to discuss stray gasses. Clair Claiborne stated Michel Duval has a good point.

Chair : Need more commentary , looking  for help  and the same for C1. (data produced by Dave Hanson). Clair would be satisfied with commentary on purpose.

Rainer Frotscher:  why UV data included? There is no UV in transformers. Answer by Dave Hanson:  UV data is important per during sampling and testing an need to add commentary

Working Group declined to address Item 5 so additional text will be added to explain the table application to DGA for re-balloting.

Chair: I will get general committee password for access. Not sure if this Working Group will have another meeting before re-ballot.

Thanks to all who made comments. Chair plans to speak with Ballot Resolution Task Force.

Chair: Do we need to get Draft 5 approved by SCIF and TC before submitting to IEEE SA? Sue McNelly stated authority already exists but will double check.

Motion to re-ballot after comments are resolved. Sue

Jerry Murphy motion to re-ballot after first ballot comments are resolved, Don Cherry 2nd motion.

Will vote on re-ballot once Draft 5 is available.

Meeting adjourned at 10:40

#### WG  PC57.637 Guide for the Reclamation of Insulating Oil and Criteria for Its Use

WG Chair Jim Thompson

The WG Report at the Sub-Committee Meeting: Presented by Jim Thompson:

The PAR for this Guide will expire at the end of 2014.

A WG Ballot (Draft 5) has been completed. Comments from the straw ballot are being reviewed.  The Chair has been asked to make available the comments that were received for posting on the web site and to his WG.  He indicated he expects to have initial responses to the comments complete by December. The goal is to proceed to ballot.  The SC Chair reminded the WG Chair that the requirement for a 2/3 majority from the WG must be met prior to going to the SC for approval to go to ballot.

The Minutes (unapproved) of C57.637 WG Meeting as Submitted:

October 22, 2013 Unapproved Minutes Working Group Meeting IEEE PC57.637, IEEE PES, Transformer Committee, Insulating Fluids Subcommittee, Working Group for the “IEEE Guide for Reclamation of Insulating Oil and Criteria For Its Use”

The working group meeting was conducted at 8 am on October 22, 2013 at St. Louis, Missouri with 42 people in attendance and with 13 of the 15 current working group members present.  This document was reaffirmed in 2007 and the PAR for revision was approved December 10, 2008.  A PAR extension request was approved until December of 2014.  Working Group member Jim Thompson (chair) conducted the meeting.

The minutes for the F12 (fall 2012) meeting were reviewed.  The F12 minutes approval, motion by Don Cherry and second by Jim Graham, was followed by unanimous approval.

The final sections had been submitted by the volunteers and reviewed as draft 3 at the F12 meeting.  The document has been provided to the working group members for straw ballot and is still in review process.  The expected completion time for this review is 6 weeks.

The chair invited wg members to discuss their comments.  The meeting discussion then included one question about table 1 in the document regarding a similar table in C57.106.  There was a general consensus however, after discussion, that a notation in table 1 referencing the C57.106 document would be sufficient.

After straw ballot review the goal is to proceed towards ballot.

Respectfully submitted,  Chair Jim Thompson

#### TF on Moisture in Oil

#### Chair: Bob Rasor

#### The TF Report given at the Sub-Committee Meeting by Claude Beauchemin:

The TF reviewed the data collection that has been performed. There was no quorum of the TF, but a consensus vote of those present indicated it was time to complete the TF activities and pass the data collected to date to the new WG on Moisture in Insulation that has been started in the Insulation Life SC.

A motion by Clair Claiborne, seconded by Don Cherry to terminate the TF was made in the IFSC meeting. During discussion of the motion, Valery Davydov on behalf of the SCIL WG expressed thanks for the work done on this by the TF. The motion approved was unanimously approved.

The Minutes (unapproved) of TF on Moisture in Oil as Submitted:

October 22, 2013. 16H45

Attendees:  63

Members: 14 out of 62: No Quorum

Chair: Bob Rasor (proxy by Claude Beauchemin)

Secretary: Hali Moleski (absent due to maternity leave)

Valery Davidov took the minutes)

Review of past year activities:

There were two phone conferences over the summer to review the data accumulated and to evaluate the future of the TF. It is the opinion of the active members that the work should be completed, the data transferred to the new C57.162 and the TF disbanded.

Bob Rasor had to excuse himself due to urgent family matter and Claude Beauchemin acted as TF chair for the time of the meeting. Hali Moleski had to excuse herself due to maternity leave.Valery Davydov was also present as acting secretary.

A review of the TF scope was presented, followed by a review of some of the data collected since the TF formation in 2009.

The objectives of the TF had been meet:

1- Obtain moisture data from several sources: Owners, Laboratories, manufacturers and repair facilities as well as from on-line monitors.

2- Information from literature was also collected.

A review of some of the collected data was made. The review indicate that moisture in oil is dynamic and that variations occurs for both short term periods, in hours, and for longer period such as yearly seasonal changes. These variations are sufficiently large to cause the actual ppm limits (such as 25and 35) to be exceeded for some time.

No motions were presented due to the absence of quorum.

A show of hand with the present attendees indicated that the general opinion was to complete the work and disband the TF. One member suggested to compute RS value from the KF data (the 22 350 points data set) for comparison purpose.

Meeting adjourned at 15H15.

Thanks to everyone for the work.

#### TF on Consolidation of Insulating Fluid Guides –

#### Chair: Tom Prevost

#### The TF Report given at the Sub-Committee Meeting by Tom Prevost:

The first meeting of this TF met Monday morning. All who applied to be members of the TF were accepted.  Information on the history behind the formation of the TF was provided.  The effort will involve review of what will be required to combine the 4 existing insulating liquid guides.  An actual PAR for this work cannot be requested until work presently in progress on C57.106, C57.121, and C57.147 has been completed nor can a draft be issued.  In the meantime, the TF will work in parallel on document structure, comparison of test methods used in the individual guides, and whether circuit breakers need to still be addressed in the service-aged oil table in C57.106.

The Minutes (unapproved) of TF on Consolidation of IF Guides as Submitted:

Task Force  - Combination of Oil Guides

Tom Prevost Chair

IEEE Meeting St. Louis Monday 10/21/2013

There were 66 people attending the meeting.

26 Requested memebrship.

General scope is to look at combining four guides into one document with the overall intent to reduce the number of (complimentary) standards.

This process originated in the Insulating Fluids subcommittee, for more info see the Fall 2011 minutes

It was noted that future revisions may be difficult.

The four documents are:

C57.106

C57.111

C57.147

C57.121

This document will focus on maintenance guides only and not anything to do with the guides for DGA

Many comments from the floor, most were positive, some had concerns.

Status of current guides

C57.106 is in the revision process, expect completion before 12/2015 which is when the PAR expires.

Bob Rasor gave an update on the current state of the work.

Some questions were raised on whether or not historical CB oil data would be included in the new guide since some thought this was part of C37 work. Others felt it would be necessary to keep this in the new guide.

Jerry Murphy and Paul Bowman offered to liaison with C37 to get advice on the matter.

C57.111 Silicon fluids has just been re-affirmed and has a 2019 revision date.

There was however a suggestion to bring current test methods (D1816) as they are not currently referenced in 111.

C57.121 amendment underway, revision due 2019, not a lot of work left to be done on the measurement.

C57.147 (new) natural esters - work is proceeding Patrick McShane leading effort

Question was raised about acceptance values.

SA note, we can’t submit a PAR for this task force (to become a WG) until the work on 106 & 147 is complete

Task force assignment of work groups:

- C37 liaison  to inquire about CB info relating to this guide

Jerry Murphy and Paul Bowman

- Section on mixing of fluids ???

Dave Hanson and Tommy Spitzer

- Comparison of test methods

Don Cherry, Clair Claiborne, Jimmy Rasco, Patrick McShane

- Document structure

Jim Graham, Tom Prevost, Jerry Reeves, Bob Rasor

Regarding the new Task Force and the proposed guide: Paul Griffin made a request to include such info as type test vs. routine test

Another request was made to have word documents of the existing guides made available?

Respectfully submitted

Mario Locarno; acting secretary

Please note the position of secretary for this task force still needs to be filled.

#### TF on Particle Count Limits in Mineral Oil

Chair: Mark Scarborough, Secretary: Paul Boman

A meeting of this TF was not held in St. Louis. The Chair, Mark Scarborough, has indicated that a final report on the information collected has been started, but is not yet ready for comment.

### New Business:

As a result of Susan McNelly moving into the Transformer Committee Secretary position starting January 1, a new WG Chair will be needed.  It was announced that David Wallach has agreed to take on this role.  The SC will be in great hands.  Thank you David!

Respectively Submitted, Patrick McShane SCIF Secretary