## ANNEX A Bushings Subcommittee

November 04, 2015

Memphis, Tennessee USA

## Chair:  Peter Zhao was unable to attend, therefore JD Brafa filled in as Chair for this meeting
Secretary:  Eric Weatherbee

- Opening of the Meeting

A.1.1   Introductions

The Chair opened the meeting with group introduction.

A.1.2   Attendance

Membership count was taken with the following results: 28 of 39 members were present and 102    guests, for a total of 130 attendees. There were 11 new membership requests. There was a quorum.

A.1.3   Chairman’s Remarks

The Chair asked for a motion to approve the S15 San Antonio minutes, a motion was made by Mr. Keith Ellis and seconded by Mr. Wayne Johnson with no objections

The Chair asked all of the WG chairs to please get their minutes submitted in a timely fashion for 		    hosting on the website.

The Chair informed the group of several administrative points that that were discussed during the ADCOM meeting at the start of the conference see Appendix A.

Two new members were added to the roster; the one in attendance was introduced and welcomed into the group.

The Chair presented the Standards Status Report for bushings, see Appendix B. He noted that the WG Chair for PC57.19.04 is seeking an extension of the PAR which will be reviewed during the December meeting.

- Working Group and Taskforce reports

A.2.1   C57.19.00-2004 – Keith Ellis, Chair

No Meeting was held. Mr. Ellis reviewed the standard and did not find anything in need of updating but asked the group to review and send him anything they deemed necessary to be brought up for discussion as a possible revision.

The Chair noted that the revision due date for this standard is fast approaching and thought it to be prudent to form a volunteer group to review the standard in its current form for any areas that could use updating and report back their findings at the next meeting. Several people volunteered for the task: Mr. Dave Geibel, Mr. Shibao Zhang, Mr. Jim Blackmon and Mr. Wes Knuth.

A.2.2   WG PC57.19.01-2000 – Dr. Shibao Zhang, Chair; David Wallach, Secretary

See complete minutes in Appendix C of this report.

A.2.3   C57.19.100-2012 – Tommy Spitzer, Chair (not present)

The guide was approved December 2012, as such no meeting was held.

A.2.4   WG PC57.19.04 – Scott Digby, Chair; JD Brafa, Vice Chair; Secretary, Jim Campbell

See complete minutes in Appendix D of this report.

A.2.5   IEC/IEEE 65700.19.03 – Les Rechsiedler (IEEE) and John Graham (IEC), Co-Chairs

The first dual logo standard was approved June of 2014, as such no meeting was held.

A.2.6   TF Distribution Transformer Bushings – Steven Shull, Chair; Ed Smith, Vice Chair

See complete minutes in Appendix E of this report.

A.2.7   TF Composite Bushings – John Graham, Chair (absent); Mark Rivers, acting Chair

Mr. Rivers showed a summary presentation of the survey that was sent out to the industry and which was discussed in full during the TF meeting (82 attendees). The survey was provided through Doble Engineering, which attempted to establish what the industry feels a composite bushing is and if the current definition should be revised. He informed the subcommittee that the taskforce agrees the definition needs to be updated but has not reached a consensus as to what the new definition should be. He also informed the subcommittee that the taskforce concluded that the C57.19 family of standards does not adequately cover emerging bushing technologies.

Out of 67 responses to the survey, 40% considered a Composite Bushing to have a “Non-ceramic weathershed regardless of core insulation” and an additional 35% defined it as being any bushing with a “Non-ceramic weathershed with solid dielectric core insulation”.

- External Liaison Reports

A.3.1 IEC Bushing Standards Activity – John Graham (absent), IEEE Liaison

See complete minutes in Appendix F of this report. As Mr. Graham was unable to attend this conference his submitted report was displayed for the group to read. Mr. Les Recksiedler agreed to act as backup for Mr. Graham if the need arises in future meetings.

A.3.2 IEEE 693 – Eric Weatherbee, IEEE Liaison

Mr. Weatherbee gave a brief presentation/update to the group. Some points were as follows:

1) The plan to change to dynamic FEA analysis only as a requirement for transformers was removed and will stay as a static analysis in this revision.

2) Shifting of the RRS to incorporate the natural frequency on the bushing will be required.

3)  Bushings must include the addition of conductor load interactions through either MAF (moment amplification factor) or ETF (equivalent terminal force) methods.

4) Tuned table pulse test was added for all shake table tested composites before/after the shake table test.

5) Grandfathering of bushings is still in review.

Next meeting was scheduled to take place in Pomona, CA Dec. 2-3, 2015. Anticipated Ballot will take place in the first quarter of 2016.

A.3.3 WG PC57.160 Guide for PD Meas. in Bushings and Inst. Trans. – Thang Hochanh, Chair

See complete minutes in Appendix G of this report.

- Unfinished Business

No unfinished business.

- New Business

A.5.1 Partial discharge in bushings

Mr. Ajith Varghese brought up his concerns of bushing PD after heat run testing and even for new bushings without heat run testing that is occurring more frequently. This started a long discussion with transformer OEM’s and Utility personnel echoing his concerns. Some of the comments during the discussion are as follows:

- Mr. Mike Sparlok and Mr. Kumar Mani agreed with Mr. Varghese concerns.

- Mr. Les Recksiedler said they no longer accept bushings that have this issue.

- Ms. Susan McNelly said they have concerns with venting during testing. They worry it will void their warranty. She suggested a section be added to the bushing application guide.

- Mr. Harold Moore shared some history on the issue and how it occurs. He stated when Westinghouse purchased GE bushing designs they switched from the metal can top design to glass bowl design which has better oil viewing but causes more PD problems.

- Mr. Dave Geibel offered up several comments including the following:

It’s been a problem forever in OIP bushings; they can obtain a paper on bubble evolution from Doble that goes into more detail. There have been no known in service failures due to this phenomenon. His company discourages venting as a solution as they feel it can exasperate the problem which also can happen when taking oil samples from bushings. It does occur in bushings that do not use glass sight glasses such as GSU designs and metal top designs. Small gas spaces can aggravate the issue. He also shared that their company has done extensive testing and found no problems occur due to this phenomenon.

- Mr. Kushal Singh commented that it appears to be more of an issue in recent years.

- Mr. Craig Stiegemeier stated that it may appear that it occurs more frequently today due to higher sensitivity of today’s test equipment and also because transformer OEM’s have sped up their processes. He commented that any aggressive test done by the transformer OEM can cause bubble evolution to occur and it is not just limited to heat run testing. He suggested RIP bushing designs could offer an alternative solution to avoid this phenomenon.

- JD Brafa reminded the group that PD could be caused by more serious issues besides bubble evolution as has been so far discussed. Mr. Brafa thought that it would be wise to form a group at the next meeting to investigate this issue more closely which could then provide suggestions to subcommittee on how the industry should deal with this phenomenon.

A.5.2 Dielectric temperature correction factor for newer RIP bushing designs

Mr. Marek Kronowski brought up a concern that he has issues when field testing the newer RIP bushing designs as he believes the temperature correction provided by one manufacturer is not correct for the newer bushings in its old software. Mr. Mario Larcano stated that this is a testing issue as the test values obtained must be reviewed to verify they make sense and are not being impacted by poor test methods or contamination etc...

A.5.3 Transformer OEMs providing CTs that fit only the bushing currently being used

Mr. Dave Geibel brought up the issue of Transformer OEMs making CTs to each bushing size (e.g., smaller diameter than specified in the standard). This causes issues for the end users when replacements are needed. Mr. Keith Ellis pointed out that it states in the standard that the CTs are to be made to accept the largest bushing designs allowed but the OEMs are refusing to follow it. Mr. Geibel stated that it is an important issue that needs more exposure to hopefully put an end to this practice.

- Adjournment 10:43 am