Chairman:				Stephen Shull

Meeting Date:		03/20/2013			Time:		9:30 – 10:45

Attendance:

| Members | 20 |
| --- | --- |
| Guests | 33 |
| Guests Requesting Membership | 2 |
| Total | 53 |

Meeting Minutes / Significant Issues / Comments:

Steve opened the meeting and rosters were passed out.  The members were listed on screen and by a show of hands, it was discovered that we did not have a quorum with only 20 of the 51 members in attendance.  Each of the working groups that met reported as follows.

- C57.12.36 –Distribution Substation Transformers

Jerry Murphy called the meeting to order. Introductions were made. The names of the members were projected on the screen. By a show of hands the quorum was not reached because there were 6 out of the 21 members present at the time.

The minutes of the fall meeting in Milwaukee could not be voted to be approved, and were tabled for the meeting in St. Louis.

Draft 3 of the standard was reviewed. Section 5.11.2 on fan motor voltage and frequency was discussed. Gary Hoffman provided the wording as was defined in C57.12.10. Gary mentioned that this was added to the 12.10 standard as a response to a comment during the balloting process. A comment was made to delete the term single phase for the 50 Hz motor definitions.

There were several comments on the people in attendance of whether the requirements for 50 Hz motors should be included in the standard, questioning if 50 Hz was part of its scope. Gary mentioned that the new rule was that as long as the scope of the document developed was within the scope of the PAR, it was acceptable.

Next was presented the new wording for the sudden pressure relay, which was adopted from the corrigenda of the C57.12.10 standard, and Gary Hoffman said that the new definition had been reviewed in detail in that WG and it was found to be correct.

Jerry mentioned that a draft with the changes from this meeting would be posted soon after the meeting, and encouraged the group to review it and provide comments.

The meeting was adjourned at 10:05 AM

- C57.12.20 – Overhead Distribution Transformers

The introductions of members and guests were done.

Al Traut provided the Chair’s Report.  The current PAR expires December 31, 2016.  The 10-year cycle ends December 31, 2021.

Al Traut reported that he is representing the C57.12.20 Working Group (WG) on a new Task Force whose focus is on common language amongst the various product standards.  The group is currently discussing the replacement of “mineral-oil-immersed” with “liquid-immersed”.  Al will provide an update on this topic at the next meeting of the WG.  The use of “oil” and “insulating oil” in the current standard was questioned.  Al advised that the WG on common language will include this in their future discussions.

A quorum of the WG’s members was not present (only 11 out of 35 members were present).

The minutes of the fall 2012 Milwaukee meeting were discussed but could not be approved due to a quorum not being present.  No issues were noted.

The first discussion of Old Business included a recommendation that Appendix A be kept, as is, in the C57.12.20 standard due to some Utilities still using these auxiliary mounting devices.

Next, Al Traut provided the following language for the WG to consider on the temperature requirements for gaskets.

“All gaskets shall be specified for use over a temperature range of -20oC to 120oC.  Gaskets in contact with current carrying components shall withstand the maximum temperature achieved when loaded within the limits specified in IEEE Std C57.91.”

Chuck Simmons will incorporate this language into the next draft revision.  The WG discussed requirements necessary for liquids other than mineral oil.  Gael Kennedy proposed that a statement be included in the standard requiring any gaskets used to be compatible with the liquid being specified.  This language will also be added to the next draft revision.

The addition of impedance and/or regulation requirements was discussed next.  A recent survey indicated that Users have two primary concerns; a) providing minimum impedance values such that fault current is limited to prescribed levels, and b) providing maximum impedance values directed towards setting regulation limits due to concerns with flicker, motor starting and other similar issues.  The WG agreed that, if approved, a table of impedance values will be needed in the standard with impedance based on the rated voltage.  Further discussion was directed at only providing minimum impedance values.  Gael Kennedy and Al Traut volunteered to put together a table of impedance values that the WG can discuss at the next meeting.

The group discussed information previously provided by Josh Verdell and Marty Rave on low voltage bushing mounting and stud dimensions.  Paul Buchanan and Al Traut volunteered to coordinate information on bushing requirements and present at the next WG meeting.

The WG discussed a concern that Al Traut received regarding the lack of transformer base requirements for overhead type transformers mounted on platforms.  The WG decided that information from Users on if, and how, they mount transformers on platforms is needed prior to any future discussions.  Chuck Simmons will send a survey to members of the Distribution Subcommittee on platform mounting of transformers and report back to the WG at the next meeting.

Meeting was adjourned at 11:55 AM.

- C57.15/IEC 60076-21  - Step-Voltage Regulators

Craig stated that the current IEEE C57.15-2009 and IEC 60076-21(2011) International Standards - Power Transformers - Part 21: Standard Requirements, Terminology, and Test code for Step-Voltage Regulators is available to industry.  Therefore, this was the first meeting to review this document and thus he asked those present to as for membership if they would like to be a member of the TF.

Craig presented the background of the work completed on the published versions.  The group looked at some of the technical comments from IEEE and IEC received during the approval of the last documents which are to be addressed for the upcoming revision.

Others areas to be considered for the next revision:

Cold start temperature for tap changer

Sound levels and corresponding design test.

Latest published versions of IEEE C57.12.00 and C57.12.90

Latest published versions of IEC 60076-1, 2, 3, 4, 5, 7 and 10.

Look at inclusion of references from the NETA documents.  Gail Kennedy will review and define sections to which he would provide back to Craig.

Incorporate latest IEC standards for Control tests.

Inclusion of a tap changer design test section

Craig discussed the need for a dual logo document on Load Tap Changers, which would the combination of IEC 60214-1 and IEEE C57.131.  Craig Colopy, Axel Kramer, and Bill Henning were to introduce this idea to the Power Transformer SC for review and search their support on this issue.

Meeting adjourned at 10:45 AM

- C57.12.34 – Three Phase Pad-mount Transformers

Steve Shull called the meeting to order.  To establish a quorum, the member list was displayed on the screen and those who saw their names were asked to hold up their hand.  From this count of hands, it was determined that a quorum was not established.  Steve asked that everyone introduce themselves.  Also, an attendance roster was circulated.

Jeff Schneider shared a presentation from the TF formed last meeting on the locations of the H0 bushing when a dead front primary is specified.  This was to follow up on the TF charge last to study where the location of this bushing should be placed on the faceplate of the transformer.  It was pointed out that 8.7.4.2 and 8.7.4.1 discusses these locations in light of the generic term “Neutral Bushing”.  The group discussed the location with respect to the presentation.  After some discussion, a few possible locations were suggested.  These are summarized in the following diagrams.

Some discussion time was spent on placing the grounding point on the interior tank wall with a hand hole to allow an access the connection point so that it could be disconnected for testing.  Brian Klaponski mentioned that this could impose an impedance between the Y common point and ground thus raising the potential between these points.  There was some discussion on this issue but no conclusions were reached.  Carlos Gaytan suggested that we move the bushing to the secondary side of the unit and utilize the existing location of the X0 / H0X0.  At this point, Steve Shull displayed Figure 7 and Figure 8A of the current standard.  A number of users commented that the location for the H0/X0 shown in Figure 8A might be a good location for the H0 since they would have concerns with operating personnel working around an open ground while removing elbows considering the control of these in respect to this bushing’s location.  Chuck Simmons stated that in some of the transformers his company purchases, they require an H0 and an X0.  This is required because of the load applications where the bonding between the X0 and ground pad is removed.  There was some discussion if this was allowed within the NEC.  This led to a discussion concerning the size of the ground pad and it location and neutral/ground bonding.

In conclusion, the working group came to no final recommendation on this item with all feeling it needed to be discussed further.  This concluded the meeting.

- C57.12.39 TF Tank Pressure Coordination

Carlos called the meeting to order at 1:45 PM. Introductions were made. The names of the members were projected on the screen. By a show of hands it was determined that a quorum was not reached because only 11 of the 31 members were present at the time.

The minutes of the fall meeting in Milwaukee could not be voted to be approved, and were tabled to be reviewed for the meeting in St. Louis.

Draft 2 of the project standard was reviewed, with comments as follows:

There was discussion on how to coordinate the upper limit for tank pressure with the self-venting cover design, which is included in the draft.

A question was raised about including requirements for tank integrity under vacuum. Carlos mentioned that on the review of the current standards, there was only a requirement in C57.12.10 that addressed vacuum in the tank. There were several comments about significant tank and cover wall deflection due to negative pressures of up to -5 psig.  This raised concerns that an accumulation of water could enter the unit as well a possible compromise of the electrical distances between components.  It was suggested that requirements for vacuum should be set to limit the tank wall deflection. Carlos mentioned that this subject of maximum vacuum allowed would be reviewed and would be considered in the inclusion of the body of the document.

Several comments were made about the use of Pressure Relief Device (PRD). It was mentioned that PRDs are not exclusively cover mounted, and some designs are mounted on the sidewall. It was suggested that a note should be added that indicates the use of PRD’s on pad mounted transformers must still meet all other requirements of that standard. (I.e. tamper proof, venting flow directions)

Regarding the coordination of requirements between the Pressure Relief Device (PRV), and the PRD and associated pressure-vacuum bleeder valve, it was recommended the wording be modified in 4.2.2.2.2 of the document to add “In addition to the cover-mounted pressure relief device, the tank shall also have a PRV or bleeder valve to relieve the tank pressure manually”. A note was made that operating ranges and characteristics should be added for the bleeder valve.

It was suggested and the group agreed that the Sudden Pressure Relay section be moved into the Dynamic Pressure section.

Al Traut suggested that Section 9 of the C57.12.20 standard should be added to the C57.12.39 standard as a normative annex.

A comment was made about the definition of Dynamic Pressure, with a concern about the length of the fault cycle lasting longer than 2 cycles. Carlos mentioned the 2 cycles is referenced as it relates to the withstand test requirement. It was noted that a fault can last more than 2 cycles in practice. At the end, it was suggested that this section should be left as is currently presented.

Regarding the report of the TF for PRV and PRD definitions, Carlos mentioned that the results of the user survey on the current application and requirements for these devices would be presented in the next meeting in St. Louis.

No new business was raised, and the meeting was adjourned at 2:45 PM.

- C57.12.35 – Distribution Transformer Bar Coding

The WG met on Tuesday, March 19, 2013 at 9:30 am in the Ammersee I Room of the Dolce Munich Hotel in Munich, Germany.

An agenda was presented and introductions were made. There was not a quorum present at this meeting. The Meeting Minutes from the previous meeting in Milwaukee, WI were reviewed but not approved since there was no quorum.

The Vice-Chair informed the WG that the standard has been submitted for balloting and it is undergoing the mandatory editorial review. The open balloting invitation will close on March 21, 2013. No questions were asked.

The meeting was adjourned at 9:45 am.

- TF – Transformer Efficiency and Loss Evaluation (DOE)

The Task Force on DOE Energy Efficiency of Transformers was called to order at 1:45 PM on March 19, 2013.  A hand count of the members was made and a quorum was declared.  The chairman reviewed the minutes of the Fall 2012 meeting in Milwaukee and the minutes were approved.  The chair recognized Al Traut as the acting secretary for this meeting.

The chair reported that the DOE has submitted a proposed Final Rule to the Office of Management and Budget (OMB) in November 2012.  To date the OMB has not acted on the proposal.  There is no known timeframe for OMB to complete their review.

The chair reviewed the slides that outline the results of the DOE process.  The DOE issued a NOPR on Feb 10, 2012 (see 77FR7282).  In this NOPR it recommended efficiency increases on medium voltage liquid immersed, medium voltage dry type, and low voltage dry type transformers.  The last public meeting on the NOPR was held in June 2012.  The details of the NOPR and the interpretation presented can be found on the IEEE Transformer Committee website.  This content has not changed since the Fall 2012 meeting.

There were some comments that the OMB is meeting with select groups on a confidential basis to solicit input regarding the DOE proposed Final Rule.  These groups include representatives of utilities, eg, EEI; manufactures, eg, NEMA; and core steel producers.  While details are not available it is a hopeful sign that the OMB is actively evaluating the proposed rule.

There was discussion around the energy efficiency standard activity in other countries, eg, Europe and Australia.  In these cases there appears to be more interest on power transformers than distribution transformers.  This work is not available to the public at this time.

The meeting was adjourned at 3:00 PM.

Old Business:

Steve asked if there was any old business to review and none was presented.

Chairman’s Comments:

- Steve reviewed the membership requirements of TF/WG/SC of the Transformer Committee.  This is listed below.

- Membership is automatically granted to anyone requesting it at the first meeting of a new WG or TF.

- Thereafter, membership is granted after a prospective member attends two consecutive meetings as a guest AND actively participates in the work of the TF/WG/SC. A former member may be reinstated if the same criterion is met.

- Ongoing membership is maintained by consistent attendance at TF/WG/SC meetings, participation in internal TF/WG/SC surveys, or technical/editorial contribution to the TF/WG/SC’s document or work.

- Membership may be revoked if a member fails to attend two consecutive meetings or fails to respond to two consecutive surveys. The chair has discretion in not removing members who cannot attend but are still participating via survey responses and/or other written contributions.

- Another key point not mentioned is that each TF/WG/SC Chair (or Secretary) must keep regular logs of attendance and participation and update the roster after each meeting.  This is done in our Transformer Committee AM system.  This should be used to determine our Quorum requirement for TF/WG/SC meeting business.

- The main benefit of membership is the privilege of voting on TF/WG/SC issues.

New Business:

- Steve discussed the Bushings Sub-Committee is working on C57.19.02 to lower the application of the standard back down to 95 kV BIL (15 kV nominal operating).  A new activity with the suggested title and scope was put forth as follows:

IEEE C57.19.02 Standard Performance Characteristics and Dimensions for Outdoor Distribution Apparatus Bushings

Suggested Scope:

This standard covers electrical, dimensional, and related requirements for outdoor power apparatus bushings that have basic impulse insulation levels (BILs) of less than 95kV. It provides specific values for dimensional and related requirements that are to be interpreted, measured, or tested in accordance with IEEE Std C57.19.00. Bushings covered by this standard are intended for use as components of oil-filled transformers.

The Bushings SC is looking for volunteers from the Distribution Transformers SC to meet with them and provide input for the inclusion of bushings at voltages lower than 95kV BIL for this proposed standard.  Steve indicated that schedule coordination would be sought to allow members to attend this group without having a conflict with other DTSC meetings.

- Steve brought up the need to define the term “permanently attached” as including in two standards under the SC, C57.12.34, 9.8.1 and C57.12.38, 9.1.  Steve will send an e-mail blast to the SC members for input.

- Steve presented on work being performed by ASTM similar to F2656-07 but for low-velocity impact barriers; meaning ≤5000 lbs at <40 mph.  Steve will send an e-mail blast to the SC members for input about the need as it might relate to equipment protection.  Using these comments he will pass on a combined comment back to the ASTM working group.

- Phil Hopkinson presented some interesting issues that were shared in the Wind Farm Transformer Working Group.  He said that there were more findings on hydrogen gassing in these transformers and three-phase pad-mounts 35 kV and below.  He discussed findings from the application of winding shields and how these seem to alleviate the static build up on the core and thus eliminate the Partial Discharge thus resulting in gassing.

Phil discussed the need to consider severe cold temperature applications where a new transformer might be factory filled at 70°C, immediately after drying, then installed at -40°C causing a significant drop in the liquid volume possibly exposing contacts of LB switches and causing a failure of the switch.  Phil suggested that some words be added to standards to address this issue.

Phil presented on an expressed desire by some wind farm transformer users to have a third compartment on pad-mount transformers for metering equipment and/or the LB switch control.  This would separate this equipment from the HV and LV compartments.  The concern of these wind farm operators was arc fault issues in the secondary compartment.  There was some discussing concerning this issue. Jerry Murphy shared some testing that was done by Industrial Application Society Electric Safety Workshop Group which indicated that effective arc rating of clothing would be low due to the spacing of the bushing in the transformer.  Steve Shull said that this was supported by the NESC since in this standard the effective arc rating would be 4 cal/cm2.

Steve adjourned the meeting with unanimous consent at 10:32am.