Insulating Fluids Subcommittee

April 15, 2015

San Antonio, TX

Chair David Wallach
Vice-Chair Jerry Murphy
Secretary C. Patrick McShane

# Introductions, Roll Call of Members for Quorum, Meeting Agenda Approval, F13 Minutes Approval, and Chair’s Comments

## Chair’s comments:

- The Chair reviewed some of the TC policies:

  - At all WG and TF meetings, participants in discussion must state their name and TC affiliation sponsor. For an item to be placed on the SCIF agenda, actionable items must be sent to the Chair at least 14 days in advance of the meeting. Sponsor ballots must first establish a quorum then require 2/3 of members present to approve before the draft can be sent to the Subcommittee for its approval. The WG and TF minutes are due to Patrick McShane by May 15, 2015.

  - The SCIF responsibilities were reviewed and include: Studying and reviewing the engineering aspects of electrical insulating liquid properties for use in transformers and other electrical apparatus, considering matters pertaining to acceptance, maintenance, and handling of such liquids; Determine the effect of various treatments, again in service, gas evolution and other phenomena on the liquids properties and determine the criteria for serviceability of the equipment; Developing and maintaining related standards, recommended practices and guides for such criteria; Coordinating with other technical committees, groups, societies, and associations as required.

- The Chair announced the next SCIF meeting will be held at the F15 meeting in Memphis, TN.

## Roll Call of SC members.  Quorum requirement: 24 minimum

There were 31 SC members and 27 guests in attendance at the meeting. A quorum was achieved. Three new SCIF members were welcomed:

Rainer Frotscher, Jerry Golarz, Deanna Woods

The following 5 guests requested membership in the IFSC at the S15 meeting:

Suh Joon Han, Roger Hayes, Arvin Joshi, Oscar Pinon, Kumar Mani

## Agenda Approval

SC Vote Outcome: Passed unanimously

## Corrections and Approval of minutes from Fall 2013, St. Louis, MO

Outcome: Passed unanimously

## WG & TF Reports Presented at the SC Meeting

### C57.104 – IEEE Guide for the Interpretation of Gases Generated in Oil – Immersed Transformer   (PAR Expiration: 12/31/17)

### WG Chair - Rick Ladroga, Vice-Chair - Claude Beauchemin

The report of the WG Meeting was presented at the SCIF meeting by Rick Ladroga.

The Chair reported that the quorum threshold was met. Presentations were made on a paper by F. Jacob and J. Dukran, and a presentation on a paper by Michel Duval. These will be posted on the WG web site. Mr. Duval will be asked to present at the F15 WG meeting.

The WG has collected over one million data points. Efforts continue on issues involving data management and security. One option being looked at is to contract to a 3rd party to collect, analyze and then destroy the original data collected.

The WG has 8 TFs working on assignments. The goal is upon completion of the assignments; a draft will be written and sent out for a straw vote.

See Annex I for the Minutes (unapproved) of C57.104 WG Meeting as Submitted

### C57.106 – IEEE Guide for Acceptance and Maintenance of Insulating Oil in Equipment    (PAR expiration: 12/31/15)

WG Chair: Bob Rasor, Vice-Chair: Jim Thompson, Secretary: Claude Beauchemin

The Report of the WG Meeting at the Sub-Committee Meeting was Presented by Bob Rasor:

Quorum was achieved. The WG membership was pared down from 30 to 26 members based on meeting attendance records. A draft was issued for a straw vote, which resulted in 162 comments received. The revised draft based on straw ballot resolution and meeting discussion and voting was approved unanimously by the WG. Don Cherry moved to request the SCIF to sponsor the draft for IEEE SA ballot process. Tom Prevost seconded the motion. The SCIF member vote was also unanimous.

See Annex II for the Minutes (unapproved) of C57.106 WG S15 Meeting as Submitted

### WG C57.130 – IEEE Guide for DGA During Factory Temperature Rise Tests for the Evaluation of Oil-Immersed Transformers and Reactors   (PAR expiration: 12/31/15)

WG Chair: Jim Thompson

The WG Report of the WG at the Sub-Committee Meeting was Presented by Jim Thompson.

There was no meeting held at S15. The current draft is still in the ballot resolution phase. There were no significant negatives and the draft should go out within a month for recirculation.

### IEEE C57.139 IEEE Dissolved Gas Analysis in Load Tap Changers (PAR expires 12/31/150)

WG Chair: David Wallach, Vice-Chair: Mark Cheatham, Secretary: Susan McNelly

The WG Report at the Sub-Committee Meeting: Presented by David Wallach

The WG met on the 14th, the quorum was established with 32 of the 59 members present. There were 52 guests, of which 7 requested WG membership. Draft 5 was written with the straw vote comments incorporated and the circulated prior to the S15 meeting. No comments or discussions were brought up on the draft. A motion was made and seconded with a super majority approval to submit the draft to the Sponsor Ballot for Approval.

See Annex III for the Minutes (unapproved) of C57.106 WG S15 Meeting as Submitted

### IEEE C57.147 Guide for Acceptance and Maintenance of Natural Ester Fluids in Transformers

WG Chair: Patrick McShane, Vice-Chair: Clair Claiborne, Secretary: Jim Graham

The WG Report at the Sub-Committee Meeting: Presented by Patrick McShane:

The WG meeting was held Monday, April 13th. Discussion was held about the first straw ballot went out to all the WG members in February. The 2 TFs that were formed at the F14 meeting are in the process of reviewing comments for resolution. The next draft based on the resolutions, will go out to vote in June to all names on the post S15 WG roster of members and guests. The member participation in the first straw vote was too low, so the Chair warned that participation in the 2nd straw vote is mandatory to maintain member status in the WG. The plan is to have a draft for WG super majority approval at the F15 meeting.

See Annex IV for the Minutes (unapproved) of C57.106 WG S15 Meeting as Submitted

### WG PC57.637 Guide for the Reclamation of Insulating Oil and Criteria for Its Use

WG Chair: Jim Thompson

The WG Report at the Sub-Committee Meeting: Presented by Jim Thompson

No meeting was held at S15. A draft should be ready in a few weeks for recirculation. The draft resolves the negative votes received. The SCIF Chair asked if there are any “show stoppers”, and the Mr. Thompson responded did could not recall any.

### TF on Consolidation of Insulating Liquid (Fluid) Guides

#### Chair: Tom Prevost

#### The TF Report given at the Sub-Committee Meeting by Tom Prevost:

The TF met on Monday April 13th and the quorum was achieved. The name of the TF has officially been changed to Consolidation of Insulating Liquid Guides.  There was discussion and consensus to include synthetic esters to the scope of the future PAR request. This is now possible because members who are also active in ASTM standards advised that ASTM is working on an acceptance standard for synthetic ester based insulating liquids, and it is very likely the new standard will be available by the time a PAR request from this TF will be made. A “Sub TF” will be formed to collect data and information on synthetic esters. James Gardner spoke that he had missed the WG meeting but agrees with the name change and indicated that the final name used for the PAR submission could still be changed. Mr. Prevost apologized for not having submitted the F14 TF minutes prior to the S15 meeting. As the meeting draft was written by the TF Secretary and is available, it was voted on to allow the addition of the minutes to the posted SCIF meeting minutes set.

See Annex V for the Minutes (unapproved) of C57.106 WG S15 Meeting as Submitted

### TF on Particle Count Limits in Mineral Oil

Chair: Mark Scarborough, Secretary: Paul Boman

A meeting of this TF was not held. David Wallach stated that Mark advised he might be able to attend the F15 meeting and provide a finish TF report at that time.

# Old Business

The status of the TF of the Standards Sub-Committee assigned to issue a white paper one Insulating Liquids Terms Normalization was reported by the TF Chair, Patrick McShane. He was please to advise that the TF white paper has been approved by the StdsSC and now posted on the IEEE TC web site section on Standards. Mr. McShane encouraged those involved with developing or revising existing standards to review the white paper to determine the proper use of terms and inclusions regarding insulating liquids.

Sanjay Patel put forward a message at the F15 SCIF meeting that he is concern that there is no clear guidance on acceptable limits for DGA after overload heat runs. Customer specified limits are “all over the place”. He believes that C57.130 might be a good place for the addition of limits for overload heat runs. Perhaps C57.119 would also be an acceptable place.

Representatives of Mr. Patel were not in attendance of the S15 SCIF meeting and the request will be dropped unless they (or others) bring it up in a future meeting.

# New Business

The Chair indicated that he received an inquiry from Dave Sundin regarding the status of a LoA from Eaton, as the Chair of C57.155 send a letter to Eaton advising that a LoA may be in order regarding certain patent(s) involving insulating liquid. No open discussion of LoA may be made at WG and TF meetings. However according to an IEEE SA representative, the SCIF can provide a link to the IEEE received LoA web site. The Chair will forward that information to Mr. Sundin.

# Adjournment

Approval to adjournment was made at 3:42 PM.

Respectively Submitted, Patrick McShane, Secretary SCIF

Unapproved Minutes from the S15 SCIF WG and TF meetings

Annex I – WG C57.104 Minutes

Chair’s Remarks:

The Chair expressed his appreciation to Paul Boman, Norm Fields, Claude Beauchemin, Luis Cheim, and Tom Prevost for their work on the document so far.

Rick indicated he was reminded that we are trying to create a guide that the industry in in need of, and that we need to bring the work back to center.  The issues with the data have held up work and to move forward, the plan is to work in parallel on the document and the data.

Data – Norm Field, Luis Cheim, Claud Beachemin

Data Protocol – Don Platts, Sue McNelly, Tom Prevost, Erin Spiewak

Diagnostic Methods – Michel Duval, Dave Wallach, Jim Dukarm

Case Studies – Paul Boman, Arturo Nunez

Arc Furnace TRs – Tom Lundquist

Bibliography – Jerry Murphy

Network TRs – Dave Hanson

Framework – Jim Dukarm, Dave Hanson, Rick Ladroga

Rick indicated his goal is to send out a rough draft to the TFs first and then to the WG.  A three year extension was obtained, but the goal is to get it out as quickly as possible.

IEEE Data Protocol Update - Don Platts

Don presented on the status of the data protocol.  A small group got together and proposed a solution of a third party to perform the data analysis, get a report and then have the original data would be destroyed.  This would eliminate the need for the NDA agreements.

IEEE looked into whether IEEE could be the third party.  They are looking at offering this service to all groups.  They are presently looking at the economics.  They plan to have a business case complete by the end of May and would be able to have data analyzed a month to month and a half after that.

Fredi Jacob indicated he and others would be opposed to destroying the data as this would prohibit anyone in the future from relooking at the data.  Rick indicated he agreed and this was the initial goal, however, the commercial considerations have required us to look at other options to allow us to move forward.

Luis Cheim suggested that the third party could receive the data, remove the identifiers within the data and then we could retain the data.

Erin indicated that even if this was done, it could be potentially determined still where the data came from.  Rick indicated at a minimum, the data could be kept in the format that it is provided in by the third party.  He indicated that we need to keep in mind the companies that have provided the data and comply with their requirements.  He also indicated that we should give credit to those that provided the data in the Guide.

Ricked reiterated that the data being provided is the livelihood of those providing it, so it is important to make sure that we work with them to get agreement on the best option for dealing with the data.

He extended an offer that if anyone had any other suggestions, that they were not comfortable bringing up in front of the group, they could feel free to contact him directly.

Jerry Reeves asked what will happen when in 10 years we start out with new data?  The evolution of the data and amount of data that would be available in the future will need to be kept in mind.

Software escrow or other type data security companies was suggested as an option for a third party company, which would eliminate the need to destroy the data.

Diagnostic Methods (Transformer Fault Severity) – Jim Dukarm, Fredi Jacob

NEI for Transformer DGA

NEI is Normalized Energy Intensity, expressed in kilojoules per kiloliter.

Calculated from the concentrations of dissolved methane, ethane, ethylene, and acetylene in a sample of transformer oil, NEI is directly related to the amount of fault energy dissipated in the oil.

We believe that NEI is a good basis for the numeric condition code for transformer DGA.

This presentation is based on our paper "Thermodynamic Estimation of Transformer Fault Severity," IEEE Transactions on Power Delivery, available for free download from IEEE Xplore.

Fault Gas

- Thermal and electrical faults must produce low molecular weight hydrocarbon gases (methane, ethane, ethylene, acetylene) from the transformer oil.

- The quantity of hydrocarbon gases generated is directly related to the fault energy.

- The relative proportions of the hydrocarbon gases depend on the distribution of temperatures in the region a affected by the fault.

Gases Found in Transformer Oil

Low Molecular Weight Hydrocarbon Gases: Methane, Ethane, Ethylene, Acetylene

- Electrical or thermal decomposition of oil

Hydrogen

- Electrical or thermal decomposition of oil

- Other sources:

- Electrolysis of water

- Stray gassing of hydro-refined oil

- Decomposition of cellulose

Carbon Oxides

- Decomposition of cellulose

- Oxidation of oil

Atmospheric Gases: Oxygen, Nitrogen

- Nitrogen blanketed or exposure of oil to air

Total Dissolved Combustible Gas (TDCG)

- weights methane and ethane equally with ethylene and acetylene

- is often mostly hydrogen and CO

...Not very suitable for severity assessment of thermal and electrical faults

Enthalpies of Formation of Fault Gases

Enthalpy of formation of a fault gas = energy required to form one mole of the gas from n-octane

(Note that CO and CO2 are mainly formed from cellulose insulation, not the oil.)

Normalized Energy Intensity

Normalized Energy Intensity (NEI) is kJ/kL calculated from the amounts of each of the four low molecular weight hydrocarbon gases generated since the transformer was commissioned.

where CH4, C2H6, C2H4, C2H2 denote the respective amounts of gas generated in µL/L.

If gas concentrations are reported at a Celsius temperature T other than zero (273 K), multiply the NEI as calculated above by 273=(273 + T ).

Understanding NEI

NEI is proportional to the amount of fault energy dissipated in the insulating oil.

- The NEI value is like an odometer reading for the transformer, roughly indicating accumulated deterioration.

- If the transformer's condition is not deteriorating due to abnormal stress or a thermal or electrical fault, the NEI remains constant.

- If the transformer is faulty or suering abnormal stress, the NEI increases.

- If the transformer is degassed or leaks gas, the unadjusted NEI may underestimate the degree of deterioration of the transformer.

NEI Statistics

DGA Database

For the NEI study, we used a database of 10092 transformers and 77456 DGA sample records from two large North American electric utilities.

DGA Database

For our NEI study, the transformers were divided into into Low-O2 and High-O2 subpopulations. The IEEE C57.104 WG observed that gas concentration statistics are a ected by O2 proportion.

A transformer was in the Low-O2 group if the median N2/O2 ratio (over all its DGA samples) was greater than 5.94. That corresponds to

Of course, as this working group has seen, there may be other transformer characteristics that need to be taken into account as well when deriving DGA limits.

DGA Limits for NEI

DGA limits for NEI can be derived statistically from DGA data for a population of similar transformers. For example, in our paper we used 80th, 90th, and 95th percentiles of NEI to obtain limits that performed well in comparison with 90th, 95th, and 98th percentile gas concentration limits.

Table 3: NEI DGA Limits (kJ/kL) Based on 80th, 90th and 95th Percentiles of Combined Data

Michel Duval's PFS method or statistical survival analysis can be used with NEI to obtain DGA limits that are more directly linked to probability of failure in service.

Calculating the DGA Condition Code

For some purposes it is useful to have a ner scale of condition values than 1, 2, 3, 4. One way to do this is by simple interpolation.

If the NEI value for a DGA sample is x, the sample's DGA score C is determined as follows:

- If x ≥L3, the score is 4.0.

- If L2 ≤ x < L3, the score is 3 + (x - L2)/(L3 - L2).

- If L1 ≤ x < L2, the score is 2 + (x - L1)=(L2 - L1).

- If x < L1, the score is 1 + x=L1.

The integer part of the interpolated DGA score is just the ordinary DGA condition code.

Assessment of Change

The NEI limits L1; L2; L3 are expressions of maintenance policy, designating NEI levels where increasing amounts of money can be spent for testing or mitigation.

A measure of the practical significance of an increase in the NEI value x is the corresponding increase in the DGA score C.

For example, it could be specifed that an increase ∆x in NEI is worthy of attention if:

- ∆x is larger than the uncertainty in x, and

- The corresponding score increase ∆C is larger than 0.1.

How to Use NEI

How to Apply NEI

- Collect a representative oil sample from the transformer and measure the gas concentrations.

- Calculate the NEI value x and compare with limits to obtain the DGA condition code C.

- Compare x and C with NEI value x0 and DGA score C0 of thereference sample.

- If C ≥2 and C has increased by at least 0.1 compared to its reference value C0, consider

- resampling to confirm this result, or

- increasing the sampling rate to investigate the mode and amount of gas production

- taking mitigative action or doing extra testing.

Note: Local policy may require investigation or surveillance in response to small increases of acetylene even when the increase in DGA score is insignificant.

Diagnosis

If the DGA score has not increased significantly, the Duval Triangle diagnosis based on the concentrations of methane, ethylene, and acetylene (if high enough) can be used to identify the "average" origin of the observed residual dissolved gas.

If the DGA score has increased significantly, the Duval Triangle diagnosis based on the increments of methane, ethylene, and acetylene can be used to identify the apparent nature of the process generating fault gas.

If a fault is suspected, and CO has been increasing simultaneously with NEI, involvement of cellulosic insulation in the fault can be suspected. Furan analysis may confirm.

If hydrogen is increasing but NEI is not, the most likely cause is stray gassing.

Example

Conclusions

On the basis of arguments and results presented in our paper, "Thermodynamic Estimation of Transformer Fault Severity," we believe that: I NEI is sensitive to each of the IEC transformer fault types.

- The overall fault sensitivity of NEI can be adjusted with predictable effect by modifying the limits.

- Because NEI is based on all the hydrocarbon gas concentrations, not just on one at a time, it responds well to gradual increases in fault severity.

- A DGA condition code based on NEI is directly related to the amount of fault energy expended in the oil, even for arcing-type faults.

Diagnostic Methods (Duval Pentagon) – Claud Beauchemin

Time ran out before this presentation could be presented.

The meeting was adjourned at 6:08 pm.

Rick Ladroga

WG Chair

Claude Beauchemin

WG Vice-Chair

Susan McNelly

WG Secretary

Unapproved Minutes from the S15 SCIF WG and TF meetings

Annex II – WG C57.106 Minutes

WG C57.106 Guide for Acceptance and Maintenance of Insulating Mineral Oil in Electrical Equipment

Monday, April 13th, 2015 4:45 PM

The meeting was called to order by Chair Bob Rasor at 4:50PM. Vice chair Jim Thompson and Secretary Claude Beauchemin were also present.

Introductions were done.  There were 51 attendees.  Two of the eight individuals that requested membership in D.C. (Fall 2014) attended, however because the straw ballot is complete, the working group is no longer accepting new members.  Quorum was reached as 16 of the 26 members were present.

Agenda for the meeting was reviewed.

There were 40+ members in the Fall of 2014, but because attendance was poor and many didn’t participate, the member list was reduced.  The names of the remaining 26 members were provided to determine if a quorum was reached.

With the 26 active members, 15 returned the straw ballot.  A straw ballot resolution TF was formed to resolve comments.  Members of this group included Don Cherry, Clair Claiborne, Claude Beauchemin, Jim Thompson, Jimmy Rasco, Oleg Roizman, Hali Moleski, and Bob Rasor.   This group had conference calls weekly to resolve the 162 comments.

Vote:  Motion was made to approve Fall 2014 meeting minutes by Don Cherry; seconded by Dave Hanson.   The minutes were unanimously approved.

Goal for this meeting is to review the draft and then let the WG vote to accept the draft and move to the Insulating Fluids Subcommittee.

Discussion following regarding some of the highlights (changes) in the document:

•	Fix page 11- C57.152 is now PES, not PSIM.  Then remove the rest of the sentence.

•	Add ‘mineral’ before all ‘oil’ in Purpose

•	Table 4 is after filling, before energizing – however, some processing/reclaiming is done energized.  This was noted by Scott Reed.  It was originally in 637 (Reclamation Guide), but removed.  Suggest footnote on Table 4 to say it also applies for energized processing. Don Platts recommended that Scott make a comment on the official ballot and offer a suggestion for addressing.

•	Vote:  Table 4 and whether D877 should remain with D1816.  Is D877 even still needed?  Some still use it in the field.  Section 5.2.1explains the difference in the two methods.  Should there be a footnote that lists D877 as alternative test?  Is one more recommended than the other or up to the end user?  Don Platts made a motion to remove D877 from Table 4.  This was 2nd by Tom Prevost.  Dave Wallach proposed amendment to motion, that if removed, then it should be reflected in the footnote and 5.2.1.  Don accepted the amendment.  ‘Remove D877 from Table 4; remove footnote ‘a’ and revise 5.2.1’.  Motion was 2nd by Dave Hanson.  The motion was approved.

•	Correct i.e. in section 4.3 to e.g. (line 12).

•	Vote:   6 & 7 (regarding LTCs) also list D877.  Don Platts made a motion to add a footnote to Tables 6 & 7 to say ‘Perform the dielectric strength test using either D1816 or D877 as shown in the Table above’. Motion was 2nd by Tom Prevost.  Motion passed.

•	Vote:  Bill Bartley noticed the [A3] IEEE 100 reference in the bibliography no longer exists.  Tom Prevost made a motion to remove it.  Don Cherry 2nd.  Motion passed.

Vote:  Tom Prevost motioned to move the C57.106 draft to the Insulating Fluids Subcommittee; 2nd by Dave Hanson. Motion passed with unanimous approval.

Vote:   Motion was made to adjourn by Don Cherry.  Meeting was adjourned approximately 6:30 pm.

Note: afterwards an attendee suggest the saturation limit equation (exponential vs. logarithmic) on line 11 of Section 4.5.

Unapproved Minutes from the S15 SCIF WG and TF meetings

Annex III – WG C57.139 Minutes

C57.139 - Draft IEEE Guide for Dissolved Gas Analysis of Load Tap Changers

Transformers

Tuesday, April 14, 2015

San Antonio, Texas, USA

Minutes of WG Meeting

Chair Dave Wallach called the WG meeting to order at 11:00 am.  Secretary Susan McNelly (minutes written by) was also present.  Vice-Chair, Mark Cheatham was not present.  There were 33 of 59 members present (Quorum requirement was met).  There were 52 guests present with 8 guests requesting membership.  At this point, new members will not be considered unless they substantially contribute, such as participating on the ballot resolution group.  The membership roster and attendance will be recorded in the Committee AM System.

The following guests requested membership in the WG but as mentioned above only those that substantially contribute at this late point in the document will be considered (*).

Julio Caldiera

Ismail Guner

John John

Terence Martin

Scott Reed *

Kevin Sullivan

John Progar *

Alwyn VanderWalt

Agenda:

1.	Introductory Remarks

• Rosters

• Introductions/Member Roll Call

• Approval of Minutes from Fall 2014 Meeting

2.	PAR Schedule Review

• Milestones

3.	Draft 4 Straw Ballot Comments -> Draft 5

4.	Vote to send to Ballot

5.	Refresh Ballot Resolution Volunteer list

6.	Old Business

7.	New Business

8.	Questions

9.	Adjourn

No changes or additions were made to the Agenda.

No changes or additions were made to the existing minutes. Motion to approve the Fall 2014 Washington

DC Metro Area meeting minutes was made by Don Cherry and seconded by George Forrest.  The motion was unanimously approved.

Document Status/Discussion

The PAR expires at the end of this year.  Our plan is to move this ahead into the ballot process.  Draft 5 of the document has been posted on the web site and sent to the WG members.

A motion by Don Cherry and seconded by Louis Cheim to move the document forward to the SC for approval to go to ballot.  The motion was unanimous with no dissentions.

Next Steps:

–	Mandatory Editorial Review

–	Prepare ballot pool

–	Ballot

–	Ballot resolution

–	Submit balloted document to REVCOM by October 23, 2015

Dave asked for volunteers for ballot resolution.  Volunteers from prior meetings were:

Tad Daniels

Mike Lau

Emilio Morales-Cruz

Tauhid Ansari

The above agreed that they were still willing to help with the ballot resolution.  Scott Reed volunteered to also help with this effort.

Old Business

No old business was discussed.

New Business

Peter Balma indicated that LTC factory testing is being looked at in another WG.  He asked for insight from the floor on how to identify acceptable DGA levels for this testing.  Dave indicated that this would be difficult to have limits due to the different LTC manufacturers and models and not being able to be manufacturer model specific.  The concept in this Guide is a statistical approach for field application.  LTC manufacturers, transformer manufacturers, and users could come up with agreed upon limits to apply during transformer final acceptance testing.  Rainer Frotscher indicated that items discussed yesterday was to determine limit values (low values).  He indicated that there are no absolute values in the C57.139 Guide.  He indicated that this Guide is a different approach as is meant for field application.

Jim Dukarm, Fredi Jacob, Rainer Frotscher were recognized by the Chair for their tremendous contributions to the Guide.

The meeting was adjourned at approximately 11:25 am.

Dave Wallach

Chair

Susan McNelly

Secretary

Unapproved Minutes from the S15 SCIF WG and TF meetings

Annex IV – WG C57.147 Minutes

April 13, 2015         San Antonio, TX

Chair: Patrick McShane, Vice-Chair: Clair Claiborne, Secretary: Jim Graham

Introductions/Membership Attendance/Quorum Check

Attendance

26 of 32 members present, quorum was achieved

40 guests

Total attendance = 66

4 guests requested membership

A motion to approve the agenda was made by Don Cherry, seconded by Derek Baronowski.  There were no changes or objections to the proposed agenda, and the motion passed.

A motion to approve the Spring 2014 meeting minutes was made by Don Cherry, seconded by Derek Baranowski.  There were no changes or objections to the minutes, and the motion passed.

Chair's Remarks, Patrick McShane:

Welcoming of new members:

Luis Cheim

Jermaine Clonts

Libin Mao

Discussion of C57.147 Draft 1.1 straw poll. There was an unacceptable low response from WG members. Due to the delay starting the straw vote, there was insufficient time for the ballot resolution TFs (one for editorial and the other for technical comments) to meet before this meeting.

Editorial and technical committee resolution task forces (See Attachment 1) will meet immediately after the working group meeting.

After the TFs complete their reviews and complete Draft 1.2, the second straw vote will be sent to all WG members and guests listed on the post meeting roster for comments.  Members who do not respond may lose their working group memberships.

Chair reminded the WG that the PAR expires end of 2016. The new time line must be complied with to meet that deadline.

Old Business

The Goal Accomplishment time line has been updated. See Attachment 2.

New Business

No new business

The meeting adjourned by acclamation at 3:45 pm.

Respectively submitted, Jim Graham, Secretary

Unapproved Minutes from the S15 SCIF WG and TF meetings

Annex V – TF C57.147 Minutes

Combination of Insulating Liquid Guides TF Meeting Notes

Meeting time: Monday April 14th, 2015 @ 0930

4th Meeting – Quorum was establish with 15 of 27 members.

Approval of Agenda - Don Cherry 1st. Jim Graham 2nd – Approved (All:0)

Approval of Minutes (as amended) – Don Cherry 1st. Dave Hanson 2nd – Approved (All:0)

Tom Prevost - Updates on the insulating liquid guides that ultimately will be combined.  The goal is for the individual guides to complete their processes and then flow into the new combined document.

C57.106

Bob Rasor Update

3 Formal Voltage Ranges adopted

Acceptance Straw Ballot April 14th for formal voting

Par expires end of 2015

C57.111

No Update Necessary from prior minutes (below)

Paul Bowman – Has a minor change, the revision is all set and ready for merge

C57.121

No updated Necessary from prior minutes (below)

Patrick – mentioned that the proposed changes were not going to be incorporated.   C57.121 is ready for merge

C57.147

The WG has the greatest movement and longest revision time with a Par Expiration of 2016.

Patrick McShane, WG Chair:

Currently in the revision process. One Straw Vote completed and under resolution activity.

Another Straw Vote Required before F15

New Business:

Name change? – Consolidation of Standards for Insulating Liquids

Tom Prevost asked to formally address the name change with a motion:

Don Cherry – Motion “Change the name of the task force from “Consolidation of Oil Guides” to “Consolidation of Insulating Liquid Guides”

Motion 2nd – Dave Hanson

Patrick McShane supported

Motion Passes Unanimously

Old Business:

Tables of Limits: Re-Review and Discussion on John Luksich’s tables (previously presented in Fall ‘14)

Synthetic Esters:

Tom Prevost suggests discussion Addition of Synthetic Esther liquids to Table 4

Patrick McShane – IEC/ASTM have values (test reference) for new insulating natural ester liquids. (No values for in-service natural ester fluids, but working on developing one)

Julio Caldeira w/ M&I Materials and Patrick w/ Cargill to collaborate as a new sub-task force and come up with some introductory numbers. Claire Claiborne mentioned that that IEC standard for new synthetic esters is 1992 vintage and quite old but that the values are still valid since technology has not changed

Synthetic Esther values from ASTM may be available shortly

Don Chu suggested that there may not need to separate natural and synthetic esters.

Patrick – Their values are significantly different and therefore warrant separation, similar to motor oils.

Rainer Frotscher - Various properties have differences.  IEC has two separate documents for Natural and Synthetic

Don Chu – User (sic Con Ed) does not differentiate.  Manufacturer will need to provide an Esther (natural or synthetic) that meets the specification

Tom Prevost – The guide will cover maintenance and used oil in addition to new.   This needs consideration.

Julio (ABB) – Why are limits needed if synthetic esters can be manufactured to specific specifications

Rainer – Transformer manufacturer needs to know the properties of the fluid to understand performance.

Freddy – Analogy with synthetic motor oil.  Viscosity and other properties are limited.

Don Chu – Minimum acceptable values that can be agreed between user, manufacturer, and fluid manufacturer.

New Sub-TF needs to be formed for developing for data for Synthetic Esthers. The Chair asked for volunteers:

Julio Caldeira, Patrick McShane, Nick Perjanik, Dave Hanson, Don Cherry

Voltage Class Discussion

Tom Prevost opened discussion on the question of whether or not the guide is suggesting endorsement of a fluid for a particular voltage class?

Jim Graham– Reduce Ambiguity on Ranges. Have upper or lower limits.  Also perhaps a note

Don Chu – Limits put liability on user and manufacturer.  More utilities are relying on IEEE standards as limits instead of guides.

Roger Wicks – How are new fluids addressed?  Fluid suppliers, manufacturers, and end users.  Tom Prevost agrees that new materials need to be addressed but perhaps the mechanism development is out of scope.

Adjournment at 10:46 am