- Performance Characteristics Subcommittee

October 22, 2014

Washington, DC

Chair:  	Ed teNyenhuis 
Vice Chair:	Craig Stiegemeier
Secretary:	Sanjib Som

# Introduction / Attendance

The Performance Characteristics Subcommittee (PCS) met on Wednesday, October 22nd, 2014 at 3pm with 161 people attending.  Of these, 68 were members and 93 were guests.  Prior to this meeting, the total membership of PCS was 115 members; therefore, quorum was achieved.

The vice chair distributed four rosters for four columns of seating arrangement in the room.

# Approval of Agenda

The Chair presented the agenda and proposed a motion to accept - this was seconded by Mr. Sanjib Som. It carried by unanimous vote.

# Approval of Last Meeting Minutes of Spring 2014

The chairman presented the minutes of the last meeting held in Savannah, GA, USA – March, 2014. This was proposed by Mr. Mark Perkins to be accepted as is, which was seconded by Mr. Phillip Hopkinson. The minutes were passed by unanimous vote.

# Chairman’s Remarks

The Chair stated there are 15 documents in purview of PCS.  All have a Chairperson assigned for responsibility and are on target to meet the revalidation deadline.

The following adjustment to Membership was presented: 31 Members missed 3 (or more) of the last 5 meetings and will be moved to “Guest” status.  Breakdown of the remaining 84 members will be 74 Members after the Spring 2014 meeting and 10 Corresponding Members moved to Members.  It was advised that anyone who believed there was an error should contact Craig.

The Chair also mentioned the PCS sponsored technical presentation for Thursday Oct 23rd 2014 on “Guide for the Application and Interpretation of Frequency Response Analysis for Oil Immersed Transfomers - C57.149” by Mark Lachman, Kirk Robbins, Charles Sweetser and Peter Werelius.

The following WG and Task Force reports were received next (the reports are below):

- WG on Tertiary/Stabilization Windings PC57.158		                   E. Betancourt

- WG on PCS Revisions to Test Code C57.12.90			        M. Perkins

- TF on Audible Sound Revision to Clause 13 of C57.12.90	                   R. Girgis

- WG on Non-sinusoidal Load Currents C57.110			        R. Marek

- WG on PCS Revisions to C57.12.00				                   T. Ansari

- WG Shunt Reactors C57.21					                   S. Som

- IEEE/IEC WG Wind Turbine Generator Transformers, P60076-16       D. Buckmaster

- WG on Loss Evaluation Guide C57.120				        M. Miller

- WG 3-ph Transf. Connections C57.105				        A. Bromley

- WG on Distributed Photo-Voltaic Grid Transformers C57.159	       H. Shertukde

- TF on HV & EHV Transients C57.142				       J. McBride

- WG on Neutral Grounding Devices PC57.32			       S. Kennedy

- TF on C57.109 - Through-Fault-Current Duration 		                  V. Mehrotra

- TF Core Gassing & Grounding					       D. Buckmaster

During the WG report for “IEEE/IEC WG Wind Turbine Generator Transformers, P60076-16”, there was a motion by Don Ayers (seconded by Phil Hopkinson) for the PCS to accept the document for balloting.  This document was approved by this WG.  This motion carried unanimously.

# Unfinished (Old) Business

None

# New Business

During the previous meeting in Savannah it was decided to appoint a Task Force to prepare text to insert into C57.12.00 to specify that core grounding or shielding of medium voltage transformers shall be applied to prevent electrostatic coupling with the medium voltage winding was approved.

The Task Force completed this text and it was presented to the PCS.  The report submitted by this TF was accepted for next steps (meaning the TF fulfilled its task). The TF chair motioned to send the text for C57.12.00 insertion to the Standards SC and to send the text for C57.12.90 insertion to the Dielectrics SC.  There was some debate on this motion.  The Chair stated that there should be a technical survey on the text prior to sending the text since there was insufficient time at the PCS meeting to properly review the text.  The TF chair (Mr. Buckmaster) did withdraw his motion with prejudice.  Since the meeting had to be adjourned, it was decided to send the text out for technical survey within PCS and then do an electronic motion to send the text on to the Standards SC and Dielectric SC as noted above.

Adjournment was proposed by Hemchandra Shertukde and seconded by Sam Mehta.

The meeting was adjourned at 4.15 pm.

Working Group (WG) and Task Force (TF) Reports (all unapproved)

J.7.1	WG on Tertiary/Stabilization Windings PC57.158 – Enrique Betancourt, Chairman; Steve Snyder, Secretary

The Chair Enrique Betancourt called the WG meeting to order at 9:30 am on October 20, 2014.  Vice- Chair Brian Penny was also present. A statement was made as to the Working Group’s purpose for preparing this Guide for publication and the meeting agenda was presented with no additions.

Introductions and a member roll call were taken. There were 20 members present out of 31 members accountable, thus a quorum to conduct business was attained. 39 Guests attended the meeting and 3 of them requested membership to the WG.

Hugo Flores				Efacec

José Izquierdo			Siemens Servicios

Shankar Nambi			Bechtel Power Corp.

The minutes from the Spring 2014 meeting in Savannah were presented and a motion to approve was made by Dr. Hemchandra Shertukde, seconded by Marnie Roussell and approved without comments.

- Old Business

Next Agenda item: Draft 3 of the Guide for Application of Tertiary and Stabilizing Windings

The Chair announced that the document had been distributed among WG members and that it soon would be posted at the IEEE PCS web site. The new items included in Chapter 1 of Draft 3 of the Guide were presented and briefly discussed during the session. Included are several considerations about impact of zero sequence impedance of transformation banks on electric power systems performance:

- Shift of line (phase) voltage and neutral voltage to ground during line to ground faults

- Line to neutral voltage instability by  loading of the neutral of the secondary side of Y connected banks with high zero sequence impedance

- Stable performance of Y-Y connected transformation stages when unbalanced loads do not draw current from the neutral of the secondary side

Technical follow-up sections will be provided in the Guide in support of all of these statements on how the stabilizing winding functions for various configurations and conditions.

As next Agenda Item, the necessary work to complete the original concept of this Guide was discussed, which includes Modeling of Steady State Behavior of TWs and SWs, Short Circuit Considerations to Comply with C57.12.00 and some Considerations for Evaluation of Transient Behavior of Transformers with and without Stabilizing Windings. A time table was agreed by the Group, aiming to complete discussion of Draft 3 and preparation of Draft 4 before the next Committee Meeting.

The Chair mentioned that with that plan the WG should be ready to release its first complete Draft by the Fall of 2015 meeting. The WG was requested to read and comment on Draft 3 over next two months and a vote was taken and a majority of the WG members (12 affirmative votes) agreed to conduct a web based meeting the week of Jan.12, 2015.

As a next Agenda Item, Mr. K. Vijayan presented a series of discussion topics related to application of Stabilizing Windings, aimed to help simplify specification, design and application of stabilizing windings. Some feedback was gathered during the presentation, and that material will be distributed among all WG members for complete assessment and comments (- External Tertiary Link, -No taps on tertiary, -LTC in the neutral, -Y connected test winding, instead of a delta connected one).

The last item briefly discussed by the Group was the definition of a kVA rating of a Stabilizing Winding when it is stated on nameplate. Getting close to time for adjournment, it was agreed to present a short tutorial on the subject of thermal loading of internal SWs during the next meeting of the WG (S.Patel, E.Betancourt, and other interested participants).

- New Business for the WG

With no new business brought up, the meeting was adjourned at 10:50 AM.

J.7.2	Working Group on PCS Revisions to C57.12.90 - Mark Perkins, Chairman; Craig Stiegemeier, Secretary

- Introduction of members and guests

- Mark Perkins presided over the meeting at Chair.  Craig Stiegemeier was secretary. Attendance rosters were circulated for those in attendance to record their presence and confirm their membership or guest status.

- An introduction of members was not conducted to support getting down to business.

- A review of the adjusted membership was conducted through the use of, and 37 of the 50 WG members were in attendance.  This resulted in attendance of 74% of the membership, making this meeting “official” as a quorum was reached.

- Minutes of the Savannah meeting

A review of the Spring 2014 Savannah meeting was conducted by Mark.  Ken Skinger made a motion, and it was seconded for approval of the spring minutes as written.  Minutes were approved by the membership unanimously.

- Old Business

A review of proposed changes to Section 9.3.1 was conducted.  The following proposed addition to section 3, tests for measuring losses and impedance voltage was discussed:

The benefits of this approach include:

- Single Phase or 3 Phase

- Requires no phase angle correction (more accurate)

- Source supplies only real power (0-50 A)

- Capacitors used on load side must be tuned to ZL

- Can use less expensive elements

- Practical for Field Test systems

Bernard Poulin made a point that the CT indicated as bushing CT would need to meet the accuracy requirements of the standards.  It was agreed that metering class bushing CT’s would meet this requirement.

A question of harmonics currents and their impact on the measurements was discussed.  Wave forms are typically clean sine waves as they come from the tuned circuit from the capacitor bank.

The following measurement protocol using the alternate method under discussion was reviewed:

- Tune the capacitor to the transformer impedance

- Apply impedance voltage with source

- Power Factor will be in the range of 0.9 to 1.0

- Set the current with Ammeter on Bushing CT

- Measure real power with the wattmeter

- Measure Impedance with voltmeter and Bushing CT and Ammeter

- Subtract the loss of capacitor bank (typical 0.5-2% of LL)

- Can also be used to determine the phase angle error in loss measurement system.

Baitun Yang suggested that there were other losses in the circuit besides the capacitor bank.

Bertrand Poulin expanded and noted that losses outside the capacitor bank would be measured, and that would be the manufacturer’s decision to accept those “surrounding” losses.  It would be a rather slight positive error, and in the field he felt it would be acceptable.

Mark Perkins noted that the capacitance of the capacitors will change with temperature

Pierre Riffon noted that capacitors losses change due to temperature.

The following notes were suggested for inclusion into section 9.3.19 (note that the term bushing CT was replaced by CT in Figure 18):

- An alternate method for either single phase or three phase transformers is to provide capacitive compensation for the transformer impedance at the terminals of the transformer so that the AC source need only supply the real power for the test.  Figure 18 shows the apparatus and connections for a single phase transformer for this alternate method. In this case, the wattmeter will measure the real power of the transformer under test plus the power of the capacitors, which will be very small compared to the power in the transformer. The load loss in the transformer is determined by subtracting the loss in the capacitors from the measured loss.

- For modern oil film capacitors, a loss of 0.2 watts per actual kVAR may be used unless a specific capacitor bank loss is known.  This method requires a separate CT or set of CT’s at the transformer for setting the current and measuring the transformer impedance.  Normal bushing CT’s can be used for this purpose as long as the CT and the current measuring device meet the accuracy requirement. The advantage of this alternate method is that the phase angle between the voltage and current at the wattmeter is low (closer to zero degrees) due to the capacitor compensation, so any phase angle errors in the loss measurement circuit are much less significant.

Note – Separate CT such as a bushing CT is needed for this alternate method

Figure 18 Alternate method for load loss measurement using capacitive compensation at the terminals of the transformer under test

The open discussion of the method included the following comments:

- Discussion of traceable calibration of the bushing CT.  Accuracy of using a bushing CT, and impact on mounting it on/in the transformer was discussed.  It was agreed that if bushing CT’s are used, they should be metering class to meet the accuracy requirement.

- Mark suggested that the method should be surveyed. John Herron suggested that sharing results of the testing that’s been performed using this method would help the WG to understand the real world accuracy of this method.

- A discussion of the potential of using this method in the factory.  Bertrand suggested that for factory measurements a certified CT should be used, where the bushing CT should only be used in the field.

- A suggestion was made that an externally mounted CT with appropriate accuracy and calibration could be used either on the line side or the neutral side.

- There was a question of what was meant by tuning the capacitor, which was answered that this was a matching the capacitor impedance to the transformer impedance.

- The major benefit of this method is allowing lighter and smaller components to support field measurements.

- A motion was made by Jeff Britton to survey the method, removing the “bushing” from the figure to allow the use of other than bushing CT’s and including the data.  John Herron seconded the motion.  The motion passed with all members agreeing to send out the suggested survey.

- New Business

Proposal to specify current required for the load loss measurement:

- Presently the is no allowance for using reduced current to measure load losses

- Load Loss is generally linear, so scaling load loss is accurate

- Temperature test section allows for reduced current

Sanjay Patel noted that for certain large GSU there would be an impact in measuring the stray losses.

Bertrand noted that in his experience the load loss was linear within the measurement uncertainty as long as the applied current was within 50% of rated. He also indicated that two items need considered - measured losses and reported losses.  He suggested measuring losses in other positions than the guarantee, but measuring the guarantee at the rated position at as close to full current as possible.

It was agreed to include further discussion on this topic as an agenda item.

- Attendance roll call – Before the meeting, the Working Group had 50 members.  See above for attendance, which resulted in sufficient membership present for a quorum.

- Adjournment – Jeff Britton made a motion to adjourn, John Herron seconded, and the group passed the motion to adjourn at 12:15 pm

J.7.3 - TF on Revision of Section 13 of C57.12.90, Sound Level Measurement - Chairman Dr. Ramsis Girgis, Secretary Barry Beaster.

The TF met at 1:45 PM on Monday, October 20, 2014.  Chairman Dr. Ramsis Girgis presided over the meeting.  Secretary Barry Beaster assisted with some administrative duties.

After the spring meeting, the membership had been adjusted to 36 members.  For review, an agenda of the fall meeting along with the unapproved spring 2014 minutes were circulated to all members, corresponding members, and guests in attendance at the last meeting.

The meeting was attended by 18 members, 5 corresponding members, and 63 guests for a total of 86 persons.  A quorum was established.  There were seven requests for task force membership.

After the introductions, Chairman Dr. Ramsis Girgis presided over the technical portion of the meeting. Members of the TF and PCS Subcommittee were surveyed for the 2nd time prior to the meeting with the proposed revision of section 13 of C57.12.90 and associated proposed additions / modifications to Table 18 in C57.12.00.

The chairman commented on the great return on the Survey (97%). He presented the results of this survey along with the following review of the 4 Disapprove Returns (6 comments) and the resolutions arrived at:

- A suggestion that Table 18 should emphasize the need for the customer specification to clearly specify whether the guarantee is on no – load noise or total noise of the transformer. This suggestion was adopted into the revision.

- A suggestion for applying the ambient noise conditions only to the main frequency components of the transformer noise when performing 1/3rd Octave or narrow band measurements. This suggestion was adopted into the revision.

- One member questioned the need for reference load noise levels versus Total noise levels. Since reference Load Noise levels are very different than No Load noise reference levels, the concept of Reference Total Noise levels is technically not feasible.

- A request to include the center frequency for Octave band noise measurements at 63 – 4000 Hz was deemed not necessary since such information is readily available in numerous references. Also, the text where this is to be introduced is the original text and there was need to change it.

- A request for more tutorial text on the near – field effect was deemed not necessary since such tutorial material belongs to a Guide not a Standard and is also available in published papers.

- A concern was indicated that manufacturers would use a default value for the Wall Sound – Reflection correction. The response to that concern was that the Standard provides detailed calculation formula of this correction; which is a function of the size of the transformer as well as the size and type of the sound test room.

The next subject on the agenda was whether there is a need to develop an IEEE Sound measurement / Sound Abatement Guide. The Chairman reviewed the situation with the present IEEE Guide. The PAR for the PC57.136 “Guide for Sound Level Abatement and Determination For liquid immersed Power Transformers and shunt reactors Rated Over 500 KVA” will expire at end of this year. The chairman presented an overview of the content of the present IEEE Guide as well as the IEC Guide presently being updated. He explained that the present IEEE Guide covers two areas; (1) Basic information on transformer noise and its measurements and (2) Transformer Sound Abatement.

The first area is covered extensively, and in much more up to – date details, in the upcoming Revised IEC Sound Application Guide expected to be completed in mid 2015. So, there does not seem to be a need for developing an IEEE Guide to cover the same information. The area of transformer sound Abatement, to be worth developing, will need to include up to date information; which would be hard to come up with since such technologies are proprietary to the individual transformer manufacturers. The chairman requested input on this subject from the floor. None in attendance felt the need for the development of an IEEE Guide or for the PAR to be extended. Steve Antosz, who assumed the owner of the PAR, stated that the Guide will still exist in its present form. It was noted, however, that much of the technical information in this Guide is well out of date. All agreed with the decision to let the PAR expire and that there is no need to develop a new Guide or upgrade the present Guide at this time. This subject may be revisited later on.

The final item on the Agenda was the development of reference Load noise levels corresponding to the NEMA levels for No – Load noise. First, the chairman presented tested Load noise levels of 180 (50 & 60 Hz) transformers of 20 – 400 MVA power ratings collected from 4 different major power transformer suppliers. The tested data was compared with values calculated using the “Reiplinger equation”. The data showed that the Reiplinger’s curve represents a below – average value for load noise. The tested load noise levels generally varied between 15 dB higher to 5 dB lower values calculated using the “Reiplinger equation”. The Chairman suggested that possibilities for reference load noise levels could be values that are 10 or 15 dB > values obtained using the Reiplinger equation. The Chairman then showed a comparison between the suggested Reference Load Noise levels vs. values from the NEMA TR1 table and (NEMA – 10 dB).

The chairman suggested using the “Reiplinger levels + 15 dB for reference load noise levels.  Jeewan Puri and Sanjay Patel had questions regarding whether it is more useful to users to have reference Total noise levels rather than reference No – Load noise levels and reference Load Noise levels separately. Again, the chairman stated that the concept of defining reference Total Noise levels is not technically accurate. Bertrand Poulin supported the position of having reference levels for both no – load and load noise as they have different frequency spectra. These different frequency components travel differently to the residential areas. Also, noise levels allowed during the day with the transformer highly loaded are 10 to 15 dB higher than those allowed during the night hours with the transformer lightly loaded.

A final comment was made by the chairman that agreed that there could be a way to combine the reference no – load noise levels and reference load noise levels into reference Total noise levels. However, as stated earlier, the concept of Reference Total Noise levels is still technically not feasible and could lead to designs that will result in noise issues when the transformer is lightly loaded at night.

The meeting adjourned at 3:00 PM.

J.7.4    Task Force for revision of IEEE Std. C57.110 “IEEE Recommended Practice for Establishing Liquid-Filled and Dry-Type Power and Distribution Transformer Capability when Supplying Non-sinusoidal Load Currents” - Chairman: Rick Marek

The working group met in the Fairfax Ballroom B of the Sheraton Premiere at Tysons Corner Hotel and the meeting was called to order at 3:15 PM by the Chairman. This was the first meeting of the WG and it was convened with 57 attendees. There were no previous minutes to approve since it was the first meeting.

The Chair presented the approved PAR Title, Scope, and Purpose, pointing out that the title will be revised to show Liquid-immersed instead of Liquid-filled. The purpose will also be revised to show when supplying instead of to supply.

The Chair presented a clarification that was made in the earlier history of the document concerning precision and cautioned that if a user is applying the document equations in a spreadsheet then they should pay attention to the correct number of significant digits after each operation. A reader has submitted such an error found in the document and it will be corrected in this revision.

Since this is a revision of an existing document, the Chair requested volunteers to review specific clauses to make sure the information is still current or to upgrade accordingly. The following assignments were made:

• The Introduction section will be reviewed by Tim Holdway, Sasha Levin, and Jagdish Burde

• Clause 4 will be reviewed by Chuck Johnson, Derek Foster, and Sheldon Kennedy

• Clause 5 will be reviewed by Thomas Holifield and Larry Kirchner

A question was raised concerning the source of the 0.8 factor in Table 5 by Kiran Vendante and he noted that, in certain circumstances, a 0.9 factor could be applicable, especially when using tank shielding. This generated a discussion with input from other individuals noting that different factors have been seen in practice by different manufacturers. The Chair noted that the 0.8 is an average, but asked that all commenters submit their suggestions in writing as proposals so that appropriate qualifications or additions may be made.

The Chair asked if the Annex C temperature rise test procedure was really needed and whether anyone had actually used it. No one indicated that they had used the procedure. Several manufacturers noted that they had the capability to perform direct thermal testing with power supplies capable of supplying harmonic currents. The range was from 100kVA to 1500kVA.

Dhiru Patel commented that he would like to see more guidance on how to separate the eddy and stray losses. He further commented that there was some work being performed in CSA and that he would check to see if their draft document could be provided to the WG.

A question was raised on the impact of the harmonics on the flux density inside the core and there was an explanation that it depends on the source impedance.

The Chair reminded everyone requesting to be a member that they must participate that they were expected to read the current document and to send comments. All of the volunteers were also reminded to submit their suggestions in writing.

With no further business, the meeting was adjourned at 4:22 PM.

27 requested membership and Samuel Sharpless volunteered to serve as secretary.

J.7.5 - PCS WG on “General Requirements C57.12.00” – Tauhid Ansari, Chairman; Enrique Betancourt, Secretary

The PCS Working Group on General Requirements for C57.12.00 met on Monday, Oct.20, 2014, at 4:30 PM, with 54 members and 76 guests present.   As the accountable Working Group membership stands at 89 members (71 Regular Members, and 18 Corresponding Members), we did have a quorum and were able to conduct official business.  The following 8 guests requested membership, which will become effective only after attending two (2) consecutive meetings:

Daniel Blaydon			Baltimore Gas & Electric

Javier Arteaga			ABB

Hugo Flores				Efacec USA

Leopoldo Rodriguez			Efacec USA

Scott Dennis				ABB

Sukdevh Wallia			Brookfield Power

Thomas Melle			HighVolt

Verena Pellon			Florida Power & Light

The Chairman, Tauhid Ansari opened the meeting by stating the purpose of the Working Group, to address matters pertaining only to performance characteristics in standard C57.12.00.  Following introductions, attendance sheets were circulated.

The proposed Agenda was presented by the Chair and approved by the members present (Motion by H. Shertukde, seconded by M.Perkins and carried by unanimous vote).

The minutes from the Savannah meeting were approved as submitted (Motion by J. Melanson, seconded by M. Perkins and carried by unanimous vote).

I.	Discussion on Old Business topics

A.	WG Item 97, C57.12.00 - 2010 Table 18. Routine, design, and other tests

Change Requested by: Joe Foldi – 2009 Ballot Comment

Requested Change: Could the details of the operational tests on the LTC equipment under full voltage (during No-Load test) and under full current (during Load loss test) be described here? The details of the LTC operational test should be described in C57.12.90, but the requirement for the test itself needs to be added here.

The Chair proposed to let this item pending till the next WG meeting, as Joe Foldi could not attend the meeting to provide further technical support to his request. The proposal was accepted with no comments.

B.	WG Item 100, Table 7 Nameplate Information, Core Construction Indication on Nameplate

Change requested by Bipin Patel – April 21, 2011 per email communication.

Requested Change: Suggestion to the WG on Revision of C57.12.00 to consider the following for inclusion to the nameplate requirement for large power (Class II as a starting point) transformers:

1. Core construction designation: core or shell

2. Core details: three legged, five legged, or seven legged

This request starts from the need to evaluate performance of existing and new transformers under Geomagnetic Disturbance Phenomena. The type of core plays a critical role in the thermal and electrical response of the transformers. Single phase or three phase may be obvious by looking at the transformer but core construction and details are data not always requested by users and, if so, then kept available during the transformers service life. The identification of critical large power transformers for protection or mitigation efforts for GMD will be greatly helped for future units.

The Chair opened the floor for discussion, with comments mainly related to the terminology of the request, which was finally as follows:

1. Transformer construction: “core” or “shell”

2. Core Type: Number of limbs. Number of wound limb(s)

Users can use the extra nameplate information for specification of replacements. Some manufacturers already provide that information on the nameplate and some users already specify core type as part of nameplate information. It was clarified (P.Jarman) that the requested information was necessary but not enough for GMD assessment.

The motion was made by M.Perkins, and seconded by E.Tenyhuis to send the modified proposal for survey within the WG and PCS. The motion was modified by Steve Antosz to accept the proposal within the by the Group corrected wording, before sending it for survey. The motion was approved by 29 in favor, and 1 opposed.

C.	Next Agenda Item WG Item 101 C57.12.00 -2010 New clause

Change Requested by:  V Sankar email dated 11/05/2012

Requested Change:

“In this CIGRE Guide (working group 12.15), in clause 10.11 on page 23 of 75 it is stated that 'A purchaser may also recompense the supplier with a bonus payment if the difference between and guaranteed losses will result in lower purchaser operating costs'”.

An incentive as above will give encouragement for innovations.  Request to consider this in your Working Group and include such a clause in C57.12.00 also.

The Chair opened the floor for discussion.

The proposal was considered unanimously as a commercial subject not pertaining to C57.12.00. With no further discussion, the Chair will inform Mr. V. Sankar that the request will not be considered further.

II.	New Business

D.	Requested Change WG Item 102 for C57.12.00 -2010 New clause

Change Requested by:  Joseph Melanson email dated 09/30/2014.

Requested Change: Proposal for adding gas injection tests on conservator transformers as part of standards

The Chair invited Joe Melanson to present his proposal to the WG.

Joe explained how the gas injection test has become common place in many users specifications, and some manufacturers perform the test as extra QA control, although the procedure itself is not standardized.

Steve Snyder clarified that the proposal for a new test does not belong to the PCS, and Steve Antosz recommended Joe to describe in written the proposal and to submit it to the Administrative SC.

Some users found beneficial to perform a gas injection test as a routine test, but it was general opinion that such a test has to be first designed. Transformers shipped with oil can be of concern if bubbles remain inside the tank.

As further New Business, Mrs. Tarlapally proposed to add a Power Factor acceptance criterion on C57.12.00.

Mark Perkins clarified that the subject belongs to Dielectric Tests, with no further discussion.

The meeting was adjourned at 6:00 PM (J. Melanson, S. Metha).

J.7.6 – WG for Shunt Reactors Rated Over 500 kVA, C57.21 - Chairman Sanjib Som; Secretary Arturo Del Rio

The working group met in the Ash Grove A Room of the Sheraton Tysons Hotel.  This was the First meeting of the working group.

- The meeting was called to order at 9:30 PM by Chairman Sanjib Som

- The Chairman stated that the position of Secretary was open, Mr Arturo Del Rio volunteered and the Chair requested him to take the position.

The working group C57.21 met for the first time on Tuesday October 21, 2014, at 9:30 with 55 participants. 14 requested membership.

- The meeting was opened with remarks from the WG Chair regarding the PAR approval and attendance sheets were circulated. PAR was approved on 21 August 2014 and expires in 2018.

- Since this was the first meeting for the WG, no previous meeting minutes were available.

- Meeting was followed by a presentation on loss measurement by Luc Dorpmanns, Royal SMIT Transformers, followed by discussions:

- Bertrand Poulin proposed that loss measurements be performed at rated MVA instead of rated voltage, this topic to be discussed in future meeting.  Also, a question was raised on the need to use a step-up transformer during the measurements.

- S. Som requested an explanation on how to handle uncertainties in the standard. Has to be reviewed if this is not already elsewhere (B. Poulin)

- Ed So mentioned the 6% tolerance on losses might be high compared to reachable measurement accuracy.

- L. Dorpmanns mentioned that there is no specific requirement for accuracy of the measurement system in this standard.  Review of the existing loss measurement guide is required in order to keep coordination.

- The Chair noted that interpretation of this section by two different individuals should lead to same conclusion.

- Review of current standard document for work items, asking input from the audience:

- Scope of work was reviewed from the PAR summary.

- L.  Dorpmanns to make a proposal to include variable shunt reactors (tap changer type).

- There is a CIGRE WG A2.48 on Shunt rectors with similar work in progress, brochure to be published in 2016.  Contents were shown by R. Ahuja.

- Altitude correction table, refer to C57.12.00 - Daniel Kramer, Phoenix technologies, will supply additional information.

- Review definition of linearity, rms or peak (B. Poulin).  How is it assessed?
How to measure this for higher voltage up to 1.5 pu?  AC or DC methods, should be explained in the standard (B. Poulin), these will addressed in next meeting

- Insulation class 150 or 155 for dry type to be reviewed with other IEEE standard (S. Som)

- Vibration test is now classified under “other”, proposal was made to make it a routine test (Darren Joe Meisner).

- Noise level is considered more significant as control of manufacturing as compared to vibration measurement (B. Poulin)

- Vibrations are easier to measure in the field then noise (Joe Meisner AEP) Should levels be lowered to IEC values. L. Dorpmanns stated that this was also discussed in CIGRE and current consensus is to use IEEE limits. L. Dorpmanns to provide a proposal for next meeting

- Request was made to the participants wanting to become a member to review the current standard and inform the chair which part they want to review.

- Gael Kennedy volunteered to provide inputs to section 4 unusual conditions.

Meeting adjournment: Raj Ahuja proposed and Dharam Vir seconded.

Meeting was adjourned at 10:30 am.

Chairman: Sanjib Som

Secretary: Arturo Del Rio

J.7.7    WG P60076-16 Standard Requirements for Wind Power Generator Transformers; Chairman: David Buckmaster; Vice Chair: Phil Hopkinson; Secretary: Donald Ayers

Meeting of joint IEEE-IEC Working Group

The Joint Working Group on Wind Power Transformers was held Friday and Saturday, October 17 & 18, 2014 in the Great Falls room, at the Sheraton Tysons Hotel, Tysons Corner, Virginia with representatives from both IEEE and IEC present. For the four hour meeting on Friday, 12 IEEE members, 3 IEC member and 1 guests attended. For the eight hour meeting on Saturday, 10 IEEE members and 3 IEC members attended.

The attendees reviewed the document as it was amended by the joint committee during a meeting held in Berlin plus additional comments submitted by other committee members. A discussion was held on whether to include words dealing with hermetically sealed liquid filled transformers. A. L. Hall agreed to propose language as to what constitutes a hermetically sealed liquid transformer. Mr. Hall also reviewed several other sections on which he had provided comments. He agreed to provide suggested language for each of the sections.

A lengthy discussion was held on the section dealing with incipient energy which had been significantly shortened during the Berlin meeting. It was agreed to revisit the language originally submitted with suggestions as to how to make the language broad enough to be acceptable. This discussion also led to a discussion on what constituted a compartmental type transformer with the need for a definition.

The meeting was suspended at 5:00 p.m. to be restarted on October 18 at 8:00 a.m.

The meeting reconvened at 8:00 a.m. on October 18, 2014.

The day was spent addressing comments and questions primarily presented by A. C. Hall, Stephan Voss and Rick Marek. Much of the document was re-written in efforts to address perceived weaknesses in the document as it was drafted after the joint meeting in Berlin. At the end of the meeting it was agreed that most of the issues were adequately addressed. The proposed document was put on the web site for people to review.

The meeting was adjourned at 4:45 p.m.

Respectfully submitted,

Donald E. Ayers

Secretary

The PAR expires December 2016.

Respectfully submitted,

Donald E. Ayers

J.7.8 - PC57.120 LOSS EVALUATION GUIDE FOR DISTRIBUTION AND POWER TRANSFORMERS AND REACTORS, Chair: Michael Miller, Vice-Chair: Rogerio Verdolin

Par status: Par approved

Par expiration date: December 31, 2016

Current draft being worked: D14

- Attendance

  - Members: 				10 of a total 22 members

  - Guests: 				41

  - Guests granted membership: 	2 pending requirements met.

  - Guests requested membership	2

  - Total:					51

- The meeting was called to order at 11:00 am on Tuesday, October 21, 2014.

- Michael Miller announced that he is taking over the position of the former Chair, Al Traut.  Rogerio Verdolin accepted to be the Vice-Chair of the Working Group.

- The minutes of meeting from the Working Group Spring 2014 meeting in Savannah, Georgia could not be approved since there was no quorum. To have a quorum we needed 11 members to be present.

- The purpose and scope of the PC57.120 was presented during the meeting.

- Estimate Timeline was presented during the meeting:

  - Final Draft from WG – April 2015

  - MEC (Editorial Review) – May 2015

  - Initial Ballot (30-day) – Jul 2015

  - Comment Resolution – Nov 2015

  - Re-Circ Ballot (10-day) – Dec 2015

  - Submit to REVCOM – Oct 2016

  - REVCOM Meeting – Dec 2016

- Price and cost information:

  - The draft loss evaluation guide includes examples of price and costs denominated in dollars and cents.  Working group chair Michael Miller commented on this issue in an email communication dated April 25, 2014, describing the following options being considered by the committee:

    - Create an annex for the examples so currency could be used

    - Use a generic currency sign (¤) to denote unspecified currency

    - Keep it as it is if IEEE will allow.

  - Option (i) is not recommended because moving costs into an annex does not mean that the information is not in the guide – it is simply moved to another place in the guide.  Moreover, it probably reduces the value of the examples.  The cost estimates directly relate to loss evaluation for distribution and power transformers and reactors, which is the object of the draft guide.  The examples are also integrally woven into the draft text, and the guide could accommodate this suggestion without extensive revision.

  - Option (ii) is not recommended because it likewise does not really address the legal issue and also makes the document less user-friendly. Using specific numbers with an unspecified currency sign (¤) may make the estimates more difficult to understand, and if the numbers used are recognizable as likely drawn from the U.S. (or from some other identifiable jurisdiction), then the legal problem is still present.

  - Option (iii) is not recommended, because the guide may then be read as implying that participants in developing the guide discussed appropriate levels of costs and prices.

  - Additional options were suggested:

- Substitute algebraic references for specific cost or price information.

- Use the Cost/Price Numbers but with further protections.

- The option (iv) clearly complies with the current policies, because it simply identifies cost or price categories without discussing their actual values.  We recognize that it also may not be as reader-friendly as a document that uses specific dollar amounts.

- The problem with the language in option (v) is that it refers to costs and prices, but the risk that the antitrust policy guards against is the risk of price-fixing (by buyers or sellers) or inappropriate information-sharing.

- Mike stated for the new draft D14 he would include the legal language added before the examples and also use the public information on dollars where possible.  He asked if there was any disagreement with this approach and there was none.One suggestion from Michael Miller is to refer the dollar values from public information, such as DOE.

- Wallace B. Binder stated that he has presented a spreadsheet from public cost information in previous meeting.  He agreed to send an updated version of the spreadsheet to Mike.

- Michael Miller discussed some comments from the draft D13.

- Michael Miller and Rogerio Verdolin will review the definitions and list of terms and allocate these two Sections in an appropriate place in the draft.

- Rogerio Verdolin will review the Table in the Section 4.3.1.1, Avoided Cost of Generation Capacity. A column will be added in this table with generic public information, such as DOE.

- Michael Miller and Rogerio Verdolin will work on a new draft to be discussed in the coming 2015 Spring Meeting, April 12-16, San Antonio, TX.

- The meeting adjourned at 12:15 PM

Respectively submitted,

Michael Miller, Chair

Rogerio Verdolin, Vice-Chair

J.7.9 - C57.105 – IEEE Guide for Application of Transformer Connections in Three-Phase Electrical Systems, Chair: Adam Bromley, Vice-Chair: Rogerio Verdolin

Par status: Will be submitted after this meeting

- Attendance

  - Members: 				2

  - Guests: 				24

  - Guests requested membership	14

  - Total:					40

- The meeting was called to order at 1:45 pm on Tuesday, October 21, 2014.

- This is a newly formed TF or WG without a PAR so establishing a quorum was unnecessary.

- The working group discussed the scope and the title of the new draft.

- Several suggestions and topics were discussed, such as:

  - Three-phase system or three-phase electrical system

  - Inclusion of auto-transformers

  - Rated voltage limit of the power transformer

  - Inclusion power transformer class

  - Inclusion of a purpose

- The final Title and Scope of the draft are as followed:

  - Title: IEEE Guide for Application of Transformer Connections in Three-Phase Electrical Systems

  - Scope: This guide describes transformer connections and configurations in 3-phase electrical systems. The characteristics of the various transformer connections and possible operating problems under normal or abnormal conditions are treated. All combinations of Δ and Y, grounded and ungrounded, T connected, zigzag, and certain special connections are considered. Only two-winding and auto- transformers are included.

- The meeting adjourned at 2:45 PM

Respectively submitted,

Adam Bromley, Chair

Rogerio Verdolin, Vice-Chair

J.7.10 – WG on “Distributed Photo Voltaic (DPV) Grid Transformers” PC57.159, Chairman Hemchandra Shertukde; Vice Chairman: Mathieu Sauzay; Secretary: Sasha Levin

The meeting was convened with 36 participants present, 19 of them are members (that constitutes a quorum out of 33 current members in the roster minus 4 absent corresponding members).  Four participants requested a membership.

- Old Business

- Spring 2014 Savannah Meeting Minutes were approved.

- New business

- Meeting Agenda was approved.

- 1. The previous Draft 2 of the Guide was reviewed in between the Spring and Fall 2014 meetings.  The WG thanks everyone who provided their comments and suggestions. The majority of the comments were resolved by revision of the Draft 2.  Some comments need to be further discussed.  The current Draft 3 of the IEEE Guide has been distributed to the WG for the review in advance to the Fall 2014 meeting.

- 2. The WG held an additional meeting on Sunday, October 19.  C. Gaytan, B. Jensen, S. Kennedy, A. Levin, A. Narawane, M. Sauzay, and H. Schertukde participated.

- S. Levin informed the WG on the Sunday’s discussion.

- 3. The WG discussed comments to the Draft 2 and Draft 3 of the Guide.  The following is the list of the reviewed topics of the Draft 3 and open Action Items:

1) Use a term “Inverter step-up transformer” in next revision.

- General observation: some comments were concerned with the Guide having too much of a tutorial. Do we think that tutorial aspects of the Guide are helpful and shall stay?

Some tutorial-type information can go to Annexes.

- Chapter 4.3.3 – does low voltage ride through issue is an important one to consider and shall be added to this Chapter?

E. Betancourt commented that the size of the DPV generation system is growing, the issues of complience with the interconnection standards becomes more and more important.

ACTION: “LV Ride Through” Chapter - H. Shertukde, C. Gaytan

- Chapter 5.1.1 and 5.1.2 – do we agree on the recommended row of rated output kVA and nominal voltage?

“Typical” instead of recommended.

kVA – add 3000 kVA

LV voltage - add 575 V and 690 V; HV voltage – 24940 V instead of 23000 V

- Chapter 5.1.3 – Is DETC necessary? Consideration points:

- inverter can regulate output voltage in order to match grid voltage

- DETC is a feature with lower reliability and good to be avoided, if not necessary.

Does everyone agree that reverse power flow isn’t an issue (problem) for the medium voltage, medium power transformers as DPV inverter transformers?

+/- 5% DETC is recommended. Other regulation can be specified as needed.

- Chapter 5.1.4 – is this possible and beneficial to have two LV windings of the same inverter transformer with “Y” and “D” winding connections in order to have 30 deg. voltage phase shift and reduce harmonic content (IEEE C57.129, Fig.1)?

In the system of 2 input LV windings, the voltages and excitation currents of these windings shall be in phase, therefore only identical winding diagrams can be used (2 “Y” or 2”D”).

Place note about step-down operation and connection diagram.

- Chapter 5.1.5 – LV1-LV2 impedance – measurement vs. calculation. Does Chapter describe the topic sufficiently?  S. Walia commented that LV1-LV2 impedance shall be defined and warranted for the system performance calculation.

It is recommended to measure LV1-LV2 impedance.

ACTION: S. Sarkar and V. Tendulkar will review the Chapter 5.1.5 and provide recommendations and references for the LV1-LV2 impedance test.

- Chapter 5.2.1 (plus 5.4.1) – daily day / night de-energization / energization (730 cycles / year).

B. Degenef commented that switching off a transformer at low load or no-load can create the significant voltage transients. Typically daily de-energization / energization is not recommended, but, in case is requested by the user, refer to IEEE C57.142 for the recommendations on analysis and protection. A system developer can conduct power quality study by modeling or direct measurement in the similar systems (overvoltage, resonans, etc.) and provide parameters of the transient process in the Specification.

The requirements to the standard tests proving a performance of the transformer in these conditions need to be recommended. Both parameters and tests are recommended to be included in the specification (e.g., are higher HV tests necessary? Does higher impedance necessary?)

Include notes on this aspect in Chapters on mechanical requirements, transient overvoltages, inrush current and Specification.

- Chapter 5.3.4 – we need to refine wording of the Chapter. Any comments, suggestions? Is PF consideration important? What would be “normal” and “abnormal” PFs? What are the consequences of “abnormal” one?

PF requirements and related tests are not addressed in IEEE standards on distribution transformers.

Refer to NETA and IEC (what documents?).

PF requirements and test for power transformers can be applicable – review IEEE Std 62 and C57.12.00.

ACTION: C. Gaytan will provide information on NETA document and will review related IEC standards for the relevant information on the PF requirements and tests for the distribution class transformers.

- Chapter 6.4 – recommended accessories – shall we describe accessories for liquid-immersed and dry-type transformers separately?

What are recommended accessories for the inverter dry-type transformer?

ACTION: C. Johnson will provide list of typical accessories for the dry-type inverter step-up transformers.

- Chapter 6.6 – useful warning sings – what shall we keep in the Guide, if any?

Make reference to the standards: ANSI Z535, NEMA, UL

- Chapter 7.1

– is inverter transformer a power or distribution transformer? What test requirements shall we follow?

-	Are there any tests addressing PF aspects necessary? What is the reference?

- Change term “Heat run test” to “Temperature rise test”.

- PD test is recommended as routine test for dry-type transformers and as type test for oil-immersed transformers. Test and Limits – IEEE C57.12.01 for dry-type transformers and IEEE C57.12.00 and C57.90 (or new proposal stemming from WG on wind power transformers) for liquid-immersed transformers.

4. WG discussed the timeline of the Guide Preparation and Ballot:

Schedule (PAR expiration date – 31 December 2016)

30 November 2014 – review of Draft 3 and submit comments (form was provided)

15 February 2015 – Draft 4 (final) sent to WG

30 March 2015 – review the Draft and conduct Straw Poll of WG by e-mail (2/3 majority)

12-16 April 2015 – submit Guide to Performance Characteristics Subcommittee for approval (simple majority)

? – editorial review

? - Sponsor Ballot

? – comments resolution

5. WG approved without reservation a transfer of the copyright to the Task Force White paper to the WG Chairman H. Scrtukde, so as allowing him to sumbit the paper to the appropriate IEEE PES sub-area for the publication as a Transaction Paper.

- With no old or new business the Meeting adjourned at 3:00 PM.

- Chairman: H. Shertukde

- Vice-chairman: M. Sauzay

- Secretary: S. Levin

J.7.11 - TF to Investigate the Interaction between Substation Transients and Transformers in HV and EHV Applications; Chairman - Jim McBride, Secretary – Tom Melle

- Welcome and Chair’s Remarks.  The TF objectives were presented.

- Circulation of Attendance Sheets (quorum delayed to allow additional members to arrive)

- Agenda was presented with no opposition

- The Chair requested any interested Guests please request membership at this meeting.

- The Chair briefly reviewed the CIGRE brochure work presented at the last meeting by Ms. Angelica Rocha.

- Pierre Riffon presented some transients from test on EHV disconnect switches.  The tests were a simulation of the breaking of small capacitive load to simulate de-energization of substation.  Two videos were shown one of a making operation and one of a breaking operation.  Presentation materials including videos will be made available to the group.  Sanjib Som asked if snubber circuits for HV/EHV circuits are available.  These circuits are primarily only used in medium voltage applications.

- Xose Lopez-Fernandez presented two mitigation methods that are described in detail in the CIGRE brochure on interactions.  These two methods are frequency domain severity factors and time domain severity factors.  Xose is the developer of the time domain technique.  In addition, Xose presented a high frequency model developed for the disconnect switch energization case that has been presented in our past task force meetings.  There was some agreement between major resonance frequencies of the model and the measured data.  The measured resonance occurred at 41 kHz and the simulation occurred at 50kHz.  There were some questions about the inclusion of some of this information in the revision of the C57-142 document.

- Bob Degeneff discussed new work that is beginning within CIGRE on high frequency modelling and the verification of these modeling with transient data.  The target maximum frequency range for this modeling is 500-750 kHz.  The designation for this new working group is JWG A2/C4.52.

- The Chair has begun a TF summary document based on the presentations and data gathered over the last two years.  The chair requested that the members of the task force review and provide feedback on this task force summary paper.  The chair summarized the three general failure modes for HV/EHV transformers found in the HV/EHV failures from the CIGRE brochure and other documents we have reviewed during our meetings.  The chair encouraged the members to review these failure modes and provide feedback to assist in finalizing the work of the task force.

- Quorum failed (22 members required). Approximately 18 counted.  Minutes will be approved by email.

- Paul Jarmin stated that IEC has an agenda item at their upcoming meeting to consider adopting C57.142 as dual logo IEEE/IEC standard.

- A straw ballot was conducted with the task force members present.  There was unanimous agreement that HV/EHV information should added to C57.142.

- Motion to adjourn the meeting made and the meeting was adjourned at 4:25PM.

Respectfully Submitted,

Tom Melle, Acting TF Secretary

J.7.12 - WG for IEEE Standard Requirements, Terminology, and Test Procedures for Neutral Grounding Devices, PC57.32, - Sheldon P. Kennedy - Chair, Tom Melle (for Fred Elliott) WG Vice-Chair

The Neutral Grounding Devices working group was called to order at 4:45 PM on October 21, 2014.

1.	Quorum was established by a head count and confirmed by the attendance rosters after the meeting – 8 working group members were present (of 13 members) with 9 guests.

2.	The agenda was presented. Motion to approve was by Don Ayers.  It received a Second by Mike Sharp.  Agenda was approved unanimously.

3.	Minutes from last meeting approved.  Motion to approve was by Don Ayers.  It received a Second by Mike Sharp.  Minutes were approved unanimously.

4.	Tom Melle (vice chair) is maintaining the official draft document.  Draft 13 was issued prior to the meeting.

5.	Sheldon Kennedy summarized the present status of the Draft 13.

6.	Test code Annex A (normative) contains obsolete test information from old standards.  This clause will either be removed (after any significant information has been moved to the relevant device clauses) or updated to reflect existing standards.  The equipment clauses will also use references to other standards as needed to keep the information current.

7.	Sergio Panetta commented that the “Ground End” designations should be changed to “Neutral Terminal”. A motion was made by Sergio Panetta (seconded by Don Ayers) that was approved. This change will be made throughout the document.

8.	Sheldon Kennedy reported that general clauses 4-9 still contain technical material which should to be moved to specific device clauses and updated.  Then the general clause information can be deleted.

9. 	Klause Pointner reported that the Neutral Grounding Reactors clause makes no references to shared clauses 4-9 can stand alone.

10.	Clause numbering issues (tables, figures, equations) will be corrected once the new template macros are enabled.

11.	Ed teNyenhuis commented that all tables borrowed from other standards should be re-verified. This was planned for the test Annex, but will now occur throughout the entire document.

12.	The document will be reviewed for consistency of terminology for liquid immersed devices (defer to C57.12.00).

13.	A motion was made by Don Ayers (seconded by Klaus Pointner) to remove Annex A (test code) from the document. Necessary information from the test Annex will be moved to each clause.

14.	Schedule:  Updates to draft sections need to be sent to Tom Melle by November 15, 2014. Monthly web meetings will be used to attempt to finalize the draft in 2014.  A working group survey will be done after this. A Subcommittee Survey will be done before the Spring 2015 Meeting. This document must be approved by the end of 2015.

Motion to adjourn by Sergio Panetta. Seconded by Don Ayers. The meeting adjourned at 6:00 pm.

Respectfully Submitted,

Tom Melle (for Fred Elliott)

WG Vice-Chair

Sheldon P. Kennedy

Chair

J.7.13 – Task Force for revision of IEEE STD C57.109 Guide for Liquid-Immersed Transformer Through–Fault-Current Duration, Chairman - Vinay Mehrotra

The kick off meeting for revision of this guide was held in the Washington Boardroom from 9.30 to 10.45 am on Tuesday. Seven members participated in the meeting.

The participants reviewed the current guide’s title and scope. It was decided to leave the title unchanged. The current guide applies to transformers referenced in the IEEE standard C57.12.00 as categories I, II, III and IV. A question was raised by Brian Penny if this guide would apply to phase- shifting transformers or the scope needs to include them.

The purpose statement was reviewed and changes were suggested. All the participants agreed that the guide is old and need significant revisions.

It was decided to take up a PAR for revision of this guide.

Respectfully submitted

Vinay Mehrotra

TF Chair

October, 2014

J.7.14 - Task Force on Core Gassing and Grounding - Chairman: David Buckmaster, Vice Chairman: Phil Hopkinson, Secretary: Donald Ayers

The Task Force on Core Gassing and Grounding was called to order at 3:15 p.m. EST on Tuesday, October 21, 2014 at the Sheraton Tysons Hotel, Tysons Corner, Virginia.

There were 72 attendees. Twelve members were present out of a membership of 18 members. A quorum was present.

The minutes from the last meeting were reviewed. Phil Hopkinson moved and Ed teNyenhuis seconded to approve the minutes. They were approved unanimously. Gary Hoffman moved and Aniruddha Narawane seconded to accept the proposed agenda for the meeting. Acceptance was unanimous.

Based on comments submitted by Jeewan Puri and Aniruddha Narawane about moisture within the core that had not been completely removed during drying, modified language for the changes to IEEE C57.12.00 was proposed to the task force. Several proposals were made from the floor to improve the language but all proposals were eventually withdrawn after brisk discussion.

Phil Hopkinson moved that the proposed language as presented be accepted without change. Steve Shull seconded the motion. More discussion was held to clarify certain aspects of the language. The vote was 7 for and 1 abstention. The motion passed.

Gary King asked why Low-High-Low construction was not excluded from the discussion. Phil Hopkinson responded that the test was a type test and should be used for all constructions, but would not expect L-H-L to have problems. Mr. King also questioned why the work only applies to transformers 15 kV and above. Response by Messrs. Hopkinson and Buckmaster state that data collected in the field did not find issues with voltages below 15 kV.

The language for proposed changes to C57.12.90 was presented and Phil Hopkinson reviewed the background for the test. Gary King asked what the duration tolerance was on the individual steps. After discussion, Gary King made a motion that the duration be a minimum and that the title of the section be changed to “Minimum test duration …”. Steve Shull seconded the motion and the motion passed unanimously.

Don Platt asked on what tap the test would be made. The response was at rated voltage tap as stated in the proposed language. A question was raised as to why only wound cores were being addressed. Dave Buckmaster responded that not enough data existed on stacked cores to develop a definite conclusion as to possible issues. Some data is just coming in that may suggest areas to investigate, but it is too early to make conclusions.

Phil Hopkinson made a motion to accept the language as modified by Gary King’s motion. Steve Shull seconded the motion. During discussion, it was asked how many readings were to be made at each voltage level. Wally Binder made a motion to amend the original motion to add that one PD reading should be taken at the end of each level. Steve Shull seconded the motion which then passed unanimously.

The vote was then taken on Mr. Hopkinson’s motion as amended. The vote was 9 for and 1 against. The motion passed.

A motion was made by Don Ayers that the results of the Task Force be reported out to the Performance Characteristic Subcommittee. Phil Hopkinson seconded.

During discussion, Garry Hoffman offered an amendment to the motion for the task forced to seek approval for a PAR for the creation of a working groups to generate an amendment to for C57.12.00 and C57.12.90 to include the language approved by the task force. Without a second, a lengthy discussion was held. The conclusion was that the task force did not have the authority to perform the requested task. At the end of the discussion, Gary Hoffman withdrew his amendment to the motion.

A vote was then held on the motion and it passed unanimously. Since the charter of the task force has been completed, it was announced that this would be the final meeting.

A motion was made and seconded to adjourn the meeting. The vote was unanimous.

The task force was disbanded at 4:35 p.m. EST.

Respectfully submitted,

Donald E. Ayers

Secretary

Encl: Final proposed language for C567.12.00 and C57.12.90

Proposed wording to insert into IEEE C57.12.00

6.7.2.1 Grounding of Wound Cores

In medium and high voltage applications of transformers with wound cores, the transformer core shall be properly grounded to the tank. One purpose is to prevent development of a voltage across the wound core loop that could result in the dielectric breakdown of the thin insulating fluid film between the core laminations and the initiation of PD and the generation of H2 and other hydrocarbons.

It should however be noted that PD generation in transformers can possibly occur due to various other factors which may be internal and/or external to the transformer and the capacitive coupling described is one of these factors.

In order to validate that the core will not be susceptible to such discharges during normal operation, a design test, specific for this type of transformer is defined in C57.12.90, Section 10.8 with acceptance criteria in Section 10.8.4. Transformers which require this design test are those manufactured with a wound core and having a high voltage winding with nominal system voltage of 15 kV or greater.

Proposed wording to insert into IEEE C57.12.90

10.8 Special Induced-Voltage Test for distribution and class I power transformers with a wound core and having a high voltage winding with nominal system voltage of 15 kV or greater.

10.8.1 Minimum test duration and application of voltage

1. Voltage will be raised to 100% of rated volts for 30 seconds and PD will be measured and recorded.

2. Voltage will be raised to 110% of rated for 30 seconds and PD will be measured and recorded.

3. Voltage will be raised to 150% of rated and held for one minute and PD will be measured and recorded.

4. Voltage will be lowered to 140% of rated for 1 minute and PD will be measured and recorded.

5. Voltage will be lowered to 130% of rated for 1 minute and PD will be measured and recorded.

6. Voltage will be lowered to 120% of rated for 1 minute and PD will be measured and recorded.

7. Voltage will be lowered to 110% of rated for 10 minutes and PD will be measured and recorded.

PD can be measured as apparent charge in pico-coulomb (pC) or RIV in micro-volt (μV). One reading shall be made at the end of each interval.

10.8.2 Test Frequency

As an induced-voltage test applies greater-than-rated volts per turn to the transformer, the frequency of the impressed voltage shall be high enough to limit the flux density in the core to that permitted by 4.1.6.1 of IEEE Std.C57.12.00-2010. The minimum test frequency to meet this condition is given in Equation (27):

(27)

where

Et is the induced voltage across winding (V)

Er is the rated voltage across winding (V)

10.8.3 Grounding of Windings

When a transformer has one end of the high-voltage winding grounded, the other windings should be grounded during the induced-voltage test. This ground on each winding may be made at a selected point of the winding itself or of the winding of a step-up transformer that is used to supply the voltage or that is connected for the purpose of furnishing the ground.

10.8.4

Failure detection

The test is considered passed if PD recorded in step 7 of 10.8.1 does not exceed partial discharge level of 100 pC or RIV level of 100 μV.