WG Revisions to Installation of Power Transformers C57.93

Monday, April 13, 2015 11:00 AM – 12:15 PM

San Antonio, TX

Minutes of the Working Group Meeting

Chair Mike Lau called the WG meeting to order at 11:00 am on April 13, 2015.   15 of 25 members were present, so a quorum was achieved.  29 guests also attended, for a total attendance of 44.  Four guests requested membership.

A motion to approve the Fall 2014 minutes was made by Alan Peterson, seconded by Mike Miller.  The minutes were approved unanimously.  The agenda was approved by acclimation.

Mike Lau reminded the working group that the PAR expires in 2016.

Mike Lau led a discussion of testing transformers under vacuum.  There was unanimous agreement that acceptance testing should not be performed while the transformer is under vacuum.  Some users monitor the progress of vacuum processing with power factor testing or winding resistance measurements.  Monitor testing may be acceptable if the test voltages are low.  Larry Kirchner will research the maximum safe voltage for monitor testing while the transformer is under vacuum.

Joe Watson submitted proposed text covering static electrification when using pumps, including a summary of concerns regarding static electrification for incorporation into the guide.  There was consensus the guide should not specify pump running durations, only general guidance.

Derek Baranowski discussed the determination of vacuum end points using dew point measurements.  This can be done with an on-line dew point monitor or periodic discreet dew point measurements.  Dew point measurements may give false positives if the moisture freezes during vacuum processing.

The last topic discussed was cold start up and operation of ester-filled transformers.  There were concerns expressed regarding the use of pumps with ester liquids.

The working group meeting adjourned at 11:55 am.

Respectfully submitted

Mike Lau	Saurabh Ghosh	Jim Graham

WG Chair 	Vice Chair	Secretary

April 13, 2015