MINUTES OF THE MEETING OF THE HVDC CONVERTER TRANSFORMERS & SMOOTHING REACTORS S.C. IN SAN DIEGO, CA, MAR. 8, 2004

______________________________________________________________________

The S.C. met in the Cockatoo Meeting Room of the Catamaran Resort Hotel in San Diego, CA on Mar. 8, 2004 from 1:45 p.m. to 3:00 p.m.  There were 12 members and 4 guests present.  One of the guests, Roger Verdolin requested membership.  Note also that one new member was added since the Pittsburgh meeting; Tony Weekes of Manitoba Hydro.  The following are the highlights of the meeting.

- Introductions were made and the minutes of the Pittsburgh meeting were approved.  The S.C. was briefed re the Administrative S.C. meeting.

- The life of the current version of C57.129 will expire in Sept. 04.  After some discussion it was agreed by the S.C. to seek a PAR for the revision of C57.129 vs the reaffirmation option.  The Chairman stated that he would work with Bill Chiu, the Standards Subcommittee Chair, to obtain a PAR.

- Tony Weekes of Manitoba Hydro made a presentation based on a paper he co-authored; “Risk Assessment Using Transformer Loss of Life Data”.  A copy of his presentation and the paper will be distributed to S.C. members only with the minutes.  A brief introduction and reference to the paper will be included in Annex D “Overloading of HVDC Converter Transformers”.   (See 6. below).

- Peter Heinzig’s proposed addition to Annex D on how to specify overloads will be included in the next draft of Annex D.

- Lars-Erik Juhlin made a presentation of his analysis of the information contained in the report prepared by Cigre TFB B4.04/42 on converter transformer failures; “Analyses of HVDC Converter Transformer Performance”.  Very few of the failures could have been prevented by changes in the test code for converter transformers.  A number of bushing failures could have been impacted by test code.  A copy of Lars-Erik’s analyses will be provided to the Bushing S.C.  Two converter transformer failures might have been influenced if Dissolved Gas Analyses were part of the temperature rise test; especially one related to a bad connection.  However, since the temperature rise test only reflects the overall heating effects of harmonics, DGA may not indicate a problem that could occur due to possible localized overheating in service.  Lars-Erik’s analysis will be used in the process of the revision of the test code in C57.129.

- Peter Heinzig will produce a draft revision of Annex D including the specification of overload criteria and will also incorporate a reference to Tony Weeke’s presentation/paper.  He will then send the new draft to Pierre Riffon, Waldemar Ziomek and Lars-Erik Juhlin for their comments/input.

- Les Ricksiedler will make changes to Draft #1 of the revision of C57.129 based on comments/proposals in his e-mail of Aug. 22, 2003.  He will, when appropriate, include explanatory comments in the margin.  Les’s changes will be circulated to S.C. members for comment as part of Draft #2 of the revision of C57.129.

8.	Lars-Erik provided, for information to S.C. members, a copy of the portion of the most recent  catalogue of CIGRÉ publications, dealing with transformers.

The Chairman will issue Draft #2 of the revision of C57.129, based on S.C. member contributions as outlined above, prior to the next S.C. meeting.  The meeting adjourned at 3:00 p.m.

Richard F. Dudley

RFD:jl

(0414)