7.3. Insulating Fluids Subcommittee (R.K. Ladroga, Chair; Susan McNelly, Secretary)

7.3.1. Introduction/Attendance

The Insulating Fluids Subcommittee met in Dallas, Texas on Wednesday, March 14, 2007 with 19 members and 41 guests present.  The following 9 guests requested membership:

Roberto Asano Jr.
Shawn Galbraith

Mark Cheatham
Robert Ganser

Luiz Cheim
Andreas Garnitschnig

Don Duckett
Jeremy Kriska

Norman Field

Meeting Agenda

1.
Introductions

2.
Patents

3.
Minutes Approval

4.
WG Reports

5.
New Business

6.
Old Business

7.
Adjourn

Introductions were made.

Sue McNelly informed the group of the sad news of Frank Gryszkiewicz’s death on February 19th.

7.3.2. Approval of Meeting Minutes and Patent Disclosure

As required in IEEE SA Standard Boards by-law, Section 6.3.2, the IEEE patent disclosure requirements were discussed and a request was made for disclosure of any patents that may be related to the work of the WG.  No new disclosures were forthcoming.

The Minutes of the Montreal, Quebec, Canada meeting were approved as written.

7.3.3. Subcommittee Membership

There were no changes to report in the Subcommittee Roster.

7.3.4. Current Subcommittee Business

7.3.4.1. C57.104 – IEEE Guide for the Interpretation of Gases Generated in Oil – Immersed Transformers

Tuesday, March 13, 2007

Dallas, Texas

The meeting was called to order by Secretary Susan McNelly at 1:50 pm, Tuesday, March 13, 2007.  Rick Ladroga the Chair and William Bartley theVice-Chair were unable to attend.  There were 29 members, 61 guests, and 15 guests requesting membership.

Guests requesting membership were:

Jim Antweiler
Dong Kim

Ray Bartnikas
Alexander Kraetge

Luis Cheim
Tom Lundquist

Alan Darwin 
Paul Mushill

Norman Field
Scott Reed

Mary Foster
Kirk Robbins

George Frimpong
Jim Thompson

Robert Ganser Jr. 

Approval of minutes from the Fall 2006 meeting in Montreal, Quebec, Canada was requested.  The minutes were approved as written.

Introductions of attendees were made.

The IEEE Patent disclosure requirements were discussed and a request was made for disclosure of any patents that may be related to the work of the WG.  There were no responses to the request for disclosure.

Susan updated the Working Group on the status of the present C57.104 Ballot process.  The document was updated as discussed at the last meeting, sent through editorial review, and submitted to IEEE for ballot.  The ballot pool process is now complete and the Guide should be out for ballot shortly.

As background, the PAR for revision was established in 1996, and was extended in 2000, 2002, and 2004.  There were some significant negative ballots during the balloting process.  Due to the comments that were outstanding, a decision was made at the Memphis meeting to withdraw the standard.  A decision to withdraw the 1991 Guide was made at the same time because of the disagreement over the values and to stress the importance of moving ahead.  Therefore, at this time, there continues to be no approved guide available.  The intent of the impending Ballot is to get a valid Guide out and available for use in the interim while work on more complete revisions is underway.

A new PAR will be filed to start over with an immediate revision to the guide to address the remaining issues that have been raised as soon as the ballot process with the existing document is complete.  

At the Montreal meeting, several Task Forces were formed to begin the work on the next revision to the Guide.  Those Task Forces were:

1. Framework

Jim Dukarm - Chair

Tim Raymond

Dave Hanson

Jim Graham

2. Data

Tom Prevost – Chair
Claude Beuchemin

Dave Hanson
Jim Dukarm

Paul Boman
Dave Wallach

Paul Mushill
Jim Graham

Bob Ganser Jr
Joe Kelly

3. Case Studies

Brian Sparling –Chair
Jim Graham

Kent Haggerty 
Paul Bowman

Dave Wallach
Bob Ganser Jr.

Dave Hanson
Paul Mushill

Tim Raymond
Joe Kelly

Norman Field

4. Diagnostic Methods

Tim Raymond – Chair
Lance Lewand

Michel Duval
Joe Kelly

Jerry Corkran 
Norman Field

Status reports from Task Forces:

Framework:

Presentation by Jim Dukarm – “A revised framework for the transformer DGA Guide.


[image: image1.wmf]S07-Dukarm-Framew

orkPresentation.pdf


General consensus was that this was a good approach to revising the Guide.

Data:

Tom reported that work is in progress and he requested that anyone that has data to send this data to him.  He was requested to provide a format for which he would want the data provided.

Other Business:

Acknowledgement was given to Paul Boman for the thirteen gas profiles that he recently provided.

Arc Furnace Transformers – Tom Lundquist indicated that he is collecting data for Arc Furnace transformers for inclusion most likely as an Annex to the revised guide.  The issue is that the manufacturers of Arc Furnace transformers are concerned that what is considered normal for these types of transformers is considered abnormal for normal power transformers.  Jim Dukarm indicated that he would not rule out that this information could be within the Guide itself rather than as an Annex.  Tom indicated that he had three labs providing data and that anyone else with data should please contact him.

The meeting was adjourned at 3:05 pm. 

Susan McNelly

PC57.104 Working Group Secretary

7.3.4.2. C57.106 – IEEE Guide for Acceptance and Maintenance of Insulating Oil in Equipment

The Working Group for the revision of the IEEE Guide for Acceptance and Maintenance of Insulating Oil in Equipment (or IEEEC57.106) did not meet in Dallas.

The PC57.106/D6 document was successfully re-balloted in October, 2006 and then approved by the IEEE Standards Board in December, 2006.  Michelle Turner, IEEE Standards Activities, reported to the Chair that the document is currently going through a copy editor for review according to the IEEE Standards Style Manual.  Publication of the revised standard is projected for June 2007.

James A. Thompson

PC57.106 Working Group Chair

7.3.4.3. C57.139 - Draft IEEE Guide for Dissolved Gas Analysis Of Load Tap Changers

Tuesday, March 13, 2007

Dallas, Texas

Fredi Jakob called the WG meeting to order at 11:05 am, Tuesday, March 13, 2007.  WG Secretary Susan McNelly was also present.  There were 27 members and 40 guests present with 4 guests requesting membership.  

Guests requesting membership were:

Norman Field

Robert Ganser Jr.

Rowland James

Jim Thompson

Agenda:

1. Welcome and Introduction

2. Patent considerations

3. Approval of Fall 2007 minutes

4. Update on LTC-DGA data Analysis – by Dave Wallach

5. Adjourn

The IEEE Patent disclosure requirements were discussed and a request was made for disclosure of any patents that may be related to the work of the WG.  There were no responses to the request for disclosure.

Approval of minutes from the Fall 2007 meeting in Montreal, Quebec, Canada was requested.  The minutes were approved as written.

An announcement was made regarding the passing of Frank Gryszkiewicz on February 19, 2007.  He will be missed.

Update on LTC-DGA Analysis – by Dave Wallach, Jim Dukarm, and Shuzhen Xu

Dave presented a report of the work that he and a subcommittee also made up of Jim Dukarm, and Shuzhen Zu have done to date.


[image: image2.wmf]S07-C57.139-DJW_P

resentation.pdf


Shuzhen Xu presented the preliminary results of the LTC DGA data analysis that she had performed.  She reviewed her statistical analysis on the Ethylene/Acetylene ratio, discussed issues with the collected data, and the statistical methodologies used.


[image: image3.wmf]S07-ShuzhenXu-LTC

_DGA_DataAnalysis.pdf


Conclusion is that we may be able to lump several models together into one basket.  More detailed review would be required to determine this.

Fredi indicated that we should wait to see what numbers (quantity of data) that we have by the Fall 2007 meeting.  If we do not have enough, then move forward with a generic guide to provide direction on how users can obtain the data and how to evaluate it.

Fredi agreed to send out a letter to the utilities requesting data be submitted.  Comments were made that many utilities just don’t have the data or the manpower to extract the data from the records that they do have.  

The meeting was adjourned at 12:19 pm. 

Fredi Jakob

Chair
7.3.4.4. C57.147 - IEEE Guide for Acceptance and Maintenance of Natural Ester Fluids in Transformers

Tuesday, March 13, 2007

Dallas, Texas

The WG meeting was called to order at 8:00 am, on Tuesday, March 13, 2007 by the working group Chair, Patrick McShane.  Vice Chair, Clair Claiborne, and Secretary, Susan McNelly were also present.  There were 16 members present and 50 guests, with 3 guests requesting membership.  Since the Guide is essentially complete and ready for ballot, no additional membership requests will be entertained.

Meeting Agenda

1. Introductions

2. Patents

3. Minutes

4. Update

5. Review last revisions

6. Vote to Submit for Balloting

7. New Business

8. Adjourn

As required in IEEE SA Standard Boards by-law, Section 6.3.2, the IEEE patent disclosure requirements were discussed and a request was made for disclosure of any patents that may be related to the work of the WG.  No new disclosures were forthcoming.

The minutes for the Fall 2007 meeting were approved as submitted and recorded on the website. 

Patrick McShane announced the sad news of the passing of Frank Gryszkiewicz on February 19, 2007.

Update:

There are only a few updates, primarily editorial, that were made since the Montreal meeting.  

Main changes to the Guide since the Fall 2006 meeting:

· NRTL was removed from the list of acronyms and abbreviations.

· Oxidation Inhibitor – added note that the user is to contact the specific fluid manufacturer for oxidation inhibitor content.  Question was raised as to how does a user necessarily know years later whose oil was used.  This could probably be more effectively dealt with in the new application guide that will be proposed at the Fluids SC meeting on Wednesday.

· Corrosive Sulfur – added a section indicating a corrosive sulfur test and that Natural Ester Fluids naturally do not contain corrosive sulfur.  Question was raised as to whether this should be included in Table 2.  Again this is probably more appropriate in an application guide.

· Discussed the removal of the “sampled from bulk tanker” and “sampled from drums or totes” levels from Table 2.   It was decided to leave it as shown in the Draft 10 that was posted.

· Table 3 – Patrick suggested that we should consider making the Water Content (mg/kg value) 150 for both less than or equal to 69 kV and for greater than 69kV but less than 230 kV.  There was discussion and it was decided to leave the levels as shown in Draft 10 as 300 and 150 respectively.

· Annex B – reviewed the additions.  Suggestion was made that since the figure for dielectric strength was left out maybe a note indicating that there would be no change in dielectric strength values in B5, Examples of key properties of mixtures of a new natural ester with a new mineral oil should be added.  Discussed if any other key properties needed to be considered.  

Additional comments received from the floor:  

Volumetric expansion rate, etc. – In Annex B there will be comments on thermal properties added.

Low temperature viscosities should be extended to lower temperatures in Table 2.  Note: ASTM D3487 does not have properties for viscosity below 0 Celsius.

Table 2 – harmonize the order of Table 2 with C57.106.  This was previously discussed and deemed not necessary.

Clause 4.4 defined the word “longer” in the last paragraph.  The words “(equal to or greater than 15 minutes at room temperature)” after the word “longer.”  Also add the words “at room temperature” to Clause 4.3.

Percentages of efficiency and cooling  - Not identified in the oil guide, so why would we include in this guide?  These are design issues.

ASTM is working on an oxidation stability test that is more suited for natural ester fluids.

This concluded the review of Draft 10. The WG officiers will review the discussion and make revisions as appropriate. The revised draft will be submitted for formal balloting as soon as possible.

The Chair thanked all the WG and other participants contributing to this proposed guide. With a successful balloting, the work of this WG is deemed finished.

The Chair mentioned that there was discussion at the Fall 06 meeting for the possible formation of TF/WG for initiating DGA and Retrofill Guides for Natural Esters, and will be subjects of new business at the Sub Committee meeting.

The meeting was adjourned at 9:00am.

Respectfully Submitted,

Patrick McShane

PC57.139 Working Group Chair

Clair Claiborne

PC57.139 Working Group Vice-Chair

7.3.5. Old Business

C57.130 – IEEE Trial-Use Guide for the Use of Dissolved Gas Analysis During Factory Temeprature Rise Tests for the Evaluation of Oil-Immersed Transformers and Reactors - The PAR expires at the end of this year.  Tom Prevost and Rick Ladroga will work together to will try and obtain the ballot resolution information and to determine what is required to move forward with this Guide.

7.3.6. New Business

The Insulation Life SC had a discussion regarding the creation of a Task Force to determine whether a new Guide for Furan Testing is needed.  There was some discussion as to whether this TF would better belong under the Insulation Life SC or the Insulating Fluids SC.  A motion was made to start a TF to study the Furan issue with Kent Haggerty as Chair and passed.  The two SC Chairs will make a decision as to which SC this will reside under, however, the general consensus of the Insulating Fluids SC members was that it belonged under the Fluids SC.

Two new orders of business in regards to Natural Ester fluids were also raised.  A motion was made for the creation of a TF to determine the need and scope of a Guide for the interpretation of DGA in transformers filled with Natural Ester fluids.  The motion passed, however, no Chair was assigned.

A second motion was made to form a TF to investigate the need for an application guide for NE fluids.  The motion passed, however, no Chair was assigned.  The TF force would investigate, among other things, retro fill of transformers with NE fluids. 

Jim Thompson brought up that the IEEE Std 637 – IEEE Guide for the Reclamation of Insulating Oil and Criteria for its Use is due for either revision or reaffirmation.  He volunteered to Chair a WG for reaffirmation of this Guide.  The exact Standard number was not known during the meeting, therefore a motion for this was not made, however, Jim is requesting the he be allowed to begin this process.

7.3.7. Adjournment

The Subcommittee adjourned at 12:00 pm.

Next Meeting:

The Insulating Fluids Subcommittee and its Working Groups will next meet in Minneapolis, Texas during the period of October 14 – 18, 2007. 

Respectfully Submitted 

Susan McNelly

Fluids SC Secretary













_1236742125.pdf


LTC DGA DATA ANALYSISLTC DGA DATA ANALYSIS
preliminary resultspreliminary results


By By ShuzhenShuzhen XU Ph.DXU Ph.D


2007 IEEE PES Transformer Spring Meeting2007 IEEE PES Transformer Spring Meeting
Dallas, March 11Dallas, March 11thth--1515thth, 2007, 2007







OUTLINESOUTLINES


Objectives.Objectives.
Statistic analysis on gas ratio Statistic analysis on gas ratio 


R1:Ethylene/Acetylene R1:Ethylene/Acetylene 
DiscussionDiscussion







ObjectivesObjectives


Demonstrate the approach used in the Demonstrate the approach used in the 
LTC data analysis.LTC data analysis.
Discuss some issues of the collected DGA Discuss some issues of the collected DGA 
data and the methodology of statistic data and the methodology of statistic 
analysis.  analysis.  







Statistics analysis of gas ratioStatistics analysis of gas ratio


Data sources (13767)Data sources (13767)
AlliantAlliant, GPC, HSB, DUKE., GPC, HSB, DUKE.


Target models:Target models:
AS1X(1737)AS1X(1737)
AS2X(778)AS2X(778)
AS2R(14)AS2R(14)
V1X(1203)V1X(1203)
ATS1X(2815)ATS1X(2815)
ATS1R(677)ATS1R(677)
NONE(6549)NONE(6549)







Statistics analysis of gas ratioStatistics analysis of gas ratio


AS1X(1737)AS1X(1737)


22


421
HC
HCR =







Statistics analysis of gas ratioStatistics analysis of gas ratio


For the aggregated data For the aggregated data 
from all of sourcesfrom all of sources


No single distribution model can No single distribution model can 
fit the data well.fit the data well.
The best fit model: mixed The best fit model: mixed 
weibullweibull modelmodel
The data are not homogeneousThe data are not homogeneous


Probability - Lognormal


Time, (t)


U
nr


el
ia


bi
lit


y,
 F


(t
)


0.100 1000.0001.000 10.000 100.000
0.010


0.050
0.100


0.500


1.000


5.000


10.000


50.000


99.990


0.010


Probability-Lognormal


ratio-all
Lognormal-2P
MLE SRM MED FM
F=1025/S=0


Data Points
Probability Line


 
 
3/7/2007
3:44:23 PM


Probability - Weibull


Time, (t)


U
nr


el
ia


bi
lit


y,
 F


(t
)


0.100 1000.0001.000 10.000 100.000
0.010


0.050


0.100


0.500


1.000


5.000


10.000


50.000


90.000


99.990


0.010


Probability-Weibull


ratio-all
Weibull-Mixed
MLE SRM MED FM
F=1025/S=0


Data Points
Probability Line


 
 
3/7/2007
3:45:05 PM







Statistics analysis of gas ratioStatistics analysis of gas ratio


AS1XAS1X-- AlliantAlliant energyenergy


(1) Aggregated data: from (1) Aggregated data: from 
1992 to 2006.1992 to 2006.


No single distribution model can No single distribution model can 
fit the data well.fit the data well.
The best fit model: mixed The best fit model: mixed weibullweibull
modelmodel
The data are not homogeneous .The data are not homogeneous .


(2) Grouped data based on (2) Grouped data based on 
the sampling date (year)the sampling date (year)


No single distribution model can No single distribution model can 
fit the data well.fit the data well.
The best fit model is mixed The best fit model is mixed 
weibullweibull model.model.
The data are not homogeneous. The data are not homogeneous. 


ReliaSoft Weibull++ 7 - www.ReliaSoft.com
Probability - Lognormal


µ=−0.5784, σ=1.2584


Time, (t)


U
nr


el
ia


bi
lit


y,
 F


(t
)


0.100 100.0001.000 10.000
0.100


0.500


1.000


5.000


10.000


50.000


99.900


0.100


Probability-Lognormal


Data 1
Lognormal-2P
MLE SRM MED FM
F=560/S=0


Data Points
Probability Line


 
 
3/5/2007
10:17:29 AM


ReliaSoft Weibull++ 7 - www.ReliaSoft.com
Probability - Weibull


Time, (t)


U
nr


el
ia


bi
lit


y,
 F


(t
)


0.100 100.0001.000 10.000
1.000


5.000


10.000


50.000


90.000


99.900
Alliant\1996
Weibull-Mixed
MLE SRM MED FM
F=28/S=0


Data Points
Probability Line


Alliant\1997
Weibull-Mixed
MLE SRM MED FM
F=45/S=0


Data Points
Probability Line


Alliant\1998
Weibull-Mixed
MLE SRM MED FM
F=42/S=0


Data Points
Probability Line


Alliant\1999
Weibull-Mixed
MLE SRM MED FM
F=40/S=0


Data Points
Probability Line


Alliant\2000
Weibull-Mixed
MLE SRM MED FM
F=58/S=0


Data Points
Probability Line


Alliant\2001
Weibull-Mixed
MLE SRM MED FM
F=65/S=0


Data Points
Probability Line


Alliant\2002
Weibull-Mixed
MLE SRM MED FM
F=62/S=0


Data Points
Probability Line


Alliant\2003
Weibull-Mixed
MLE SRM MED FM
F=63/S=0


Data Points







Statistics analysis of gas ratioStatistics analysis of gas ratio


The data sampled on the The data sampled on the same modelsame model of units from the of units from the 
same utilitysame utility are are not homogeneousnot homogeneous..
The source of the nonThe source of the non--homogeneous.homogeneous.


Condition of the units: “healthy” and “nonCondition of the units: “healthy” and “non--healthy”healthy”
Main sourceMain source


Different breathing systems (not available)Different breathing systems (not available)----ignored.ignored.
Different labs tests (not available)Different labs tests (not available)----ignored.ignored.







Statistics analysis of gas ratioStatistics analysis of gas ratio


The effect of the condition of the units on gas ratio R1 The effect of the condition of the units on gas ratio R1 


“Healthy” LTC “Healthy” LTC 
R1 is low and remains relative constant before the unit developR1 is low and remains relative constant before the unit develops some s some 
problems. problems. 


“Unhealthy” LTC“Unhealthy” LTC
R1 is relative bigger and its value depends on how bad the problR1 is relative bigger and its value depends on how bad the problem of em of 
the sampled unit is. the sampled unit is. 







Statistics analysis of gas ratioStatistics analysis of gas ratio
Differentiate the data of the healthy unit from unhealthy unit.Differentiate the data of the healthy unit from unhealthy unit.


Assumption:Assumption:
(1) The ratio from unhealthy units have higher value. (1) The ratio from unhealthy units have higher value. 
(2) The ratio from healthy units have lower value.(2) The ratio from healthy units have lower value.
(3) The statistic distribution of the ratio of the healthy u(3) The statistic distribution of the ratio of the healthy units  from single source nits  from single source 
should follow same distribution over the time. should follow same distribution over the time. 
The approach:The approach:
(1) (1) Divide the data from a single company into different groups baseDivide the data from a single company into different groups based on the d on the 
sampling date (year).sampling date (year).
(2) Truncate the data in each group  until the following tw(2) Truncate the data in each group  until the following two criteria (differentiation o criteria (differentiation 
criteria) are met:criteria) are met:


(a) the truncated data can be modeled well by a single distribut(a) the truncated data can be modeled well by a single distribution.ion.
(b) the truncated data in all the groups follow the (b) the truncated data in all the groups follow the same distributionsame distribution. . 


(3) Repeat the above procedure for the data from other companies(3) Repeat the above procedure for the data from other companies..
(4) Aggregated the truncated data from different companies (4) Aggregated the truncated data from different companies into a single pool.into a single pool.







Statistics analysis of gas ratioStatistics analysis of gas ratio


Statistics analysis results of the truncated Statistics analysis results of the truncated 
AlliantAlliant data for each group.data for each group.


When the data truncated at 80 and 70 percentile, only criteria (When the data truncated at 80 and 70 percentile, only criteria (a) is a) is 
met.met.
Both criteria are met when the truncation is at 60 percentile vaBoth criteria are met when the truncation is at 60 percentile value.  lue.  
The data truncated at 60 percentile in each group can be consideThe data truncated at 60 percentile in each group can be considered red 
from same population statistically which represents the “healthyfrom same population statistically which represents the “healthy” ” 
units. Therefore these truncated data can be aggregated into theunits. Therefore these truncated data can be aggregated into the
same pool of “healthy” units. same pool of “healthy” units. 







Statistics analysis of gas ratio R1Statistics analysis of gas ratio R1


Cumulative probability for the truncated 
data(60%) sampled in 1996-2005


Probability density function for the truncated 
data(60%) sampled in 1996-2005


ReliaSoft Weibull++ 7 - www.ReliaSoft.com
Probability - Lognormal


Time, (t)


U
nr


el
ia


bi
lit


y,
 F


(t
)


0.100 2.000
0.100


0.500


1.000


5.000


10.000


50.000


99.900


0.100


Alliant-truncation-60\1996
Lognormal-2P
MLE SRM MED FM
F=15/S=0


Data Points
Probability Line


Alliant-truncation-60\1997
Lognormal-2P
MLE SRM MED FM
F=26/S=0


Data Points
Probability Line


Alliant-truncation-60\1998
Lognormal-2P
MLE SRM MED FM
F=25/S=0


Data Points
Probability Line


Alliant-truncation-60\1999
Lognormal-2P
MLE SRM MED FM
F=24/S=0


Data Points
Probability Line


Alliant-truncation-60\2000
Lognormal-2P
MLE SRM MED FM
F=34/S=0


Data Points
Probability Line


Alliant-truncation-60\2001
Lognormal-2P
MLE SRM MED FM
F=39/S=0


Data Points
Probability Line


Alliant-truncation-60\2002
Lognormal-2P
MLE SRM MED FM
F=36/S=0


Data Points
Probability Line


Alliant-truncation-60\2003
Lognormal-2P
MLE SRM MED FM
F=37/S=0


Data Points


ReliaSoft Weibull++ 7 - www.ReliaSoft.com
Probability Density Function


Time, (t)


f(
t)


0.100 2.0000.480 0.860 1.240 1.620
0.100


6.000


1.280


2.460


3.640


4.820


Alliant-truncation-60\1996
Lognormal-2P
MLE SRM MED FM
F=15/S=0


Pdf Line
Alliant-truncation-60\1997
Lognormal-2P
MLE SRM MED FM
F=26/S=0


Pdf Line
Alliant-truncation-60\1998
Lognormal-2P
MLE SRM MED FM
F=25/S=0


Pdf Line
Alliant-truncation-60\1999
Lognormal-2P
MLE SRM MED FM
F=24/S=0


Pdf Line
Alliant-truncation-60\2000
Lognormal-2P
MLE SRM MED FM
F=34/S=0


Pdf Line
Alliant-truncation-60\2001
Lognormal-2P
MLE SRM MED FM
F=39/S=0


Pdf Line
Alliant-truncation-60\2002
Lognormal-2P
MLE SRM MED FM
F=36/S=0


Pdf Line
Alliant-truncation-60\2003
Lognormal-2P
MLE SRM MED FM
F=37/S=0


Pdf Line
Alliant-truncation-60\2004
Lognormal-2P
MLE SRM MED FM
F=36/S=0


Pdf Line
Alliant-truncation-60\2005
Lognormal-2P







Statistics analysis of gas ratioStatistics analysis of gas ratio


Repeat the above procedure to the data from GPC (1025 data Repeat the above procedure to the data from GPC (1025 data 
point) .point) .


the nonthe non--homogeneous phenomenon is also found.homogeneous phenomenon is also found.
Both differentiation criteria are met when the truncation occursBoth differentiation criteria are met when the truncation occurs at 90 at 90 
percentile for each group. Therefore the truncated data from eacpercentile for each group. Therefore the truncated data from each h 
group can be aggregated in to the pool for the “healthy” units .group can be aggregated in to the pool for the “healthy” units .







Statistics analysis of gas ratio R1Statistics analysis of gas ratio R1
ReliaSoft Weibull++ 7 - www.ReliaSoft.com


Probability - Lognormal


Time, (t)


U
nr


el
ia


bi
lit


y,
 F


(t
)


0.100 10.0001.000
0.100


0.500


1.000


5.000


10.000


50.000


99.900


0.100


GPC-90\1997
Lognormal-2P
MLE SRM MED FM
F=62/S=0


Data Points
Probability Line


GPC-90\1998
Lognormal-2P
MLE SRM MED FM
F=84/S=0


Data Points
Probability Line


GPC-90\1999
Lognormal-2P
MLE SRM MED FM
F=92/S=0


Data Points
Probability Line


GPC-90\2000
Lognormal-2P
MLE SRM MED FM
F=95/S=0


Data Points
Probability Line


GPC-90\2001
Lognormal-2P
MLE SRM MED FM
F=90/S=0


Data Points
Probability Line


GPC-90\2002
Lognormal-2P
MLE SRM MED FM
F=95/S=0


Data Points
Probability Line


GPC-90\2003
Lognormal-2P
RRX SRM MED FM
F=97/S=0


Data Points
Probability Line


GPC-90\2004
Lognormal-2P
MLE SRM MED FM
F=103/S=0


Data Points


ReliaSoft Weibull++ 7 - www.ReliaSoft.com
Probability Density Function


Time, (t)


f(
t)


0.000 2.0000.400 0.800 1.200 1.600
0.100


6.000


1.280


2.460


3.640


4.820


GPC-90\1997
Lognormal-2P
MLE SRM MED FM
F=62/S=0


Pdf Line
GPC-90\1998
Lognormal-2P
MLE SRM MED FM
F=84/S=0


Pdf Line
GPC-90\1999
Lognormal-2P
MLE SRM MED FM
F=92/S=0


Pdf Line
GPC-90\2000
Lognormal-2P
MLE SRM MED FM
F=95/S=0


Pdf Line
GPC-90\2001
Lognormal-2P
MLE SRM MED FM
F=90/S=0


Pdf Line
GPC-90\2002
Lognormal-2P
MLE SRM MED FM
F=95/S=0


Pdf Line
GPC-90\2003
Lognormal-2P
RRX SRM MED FM
F=97/S=0


Pdf Line
GPC-90\2004
Lognormal-2P
MLE SRM MED FM
F=103/S=0


Pdf Line
GPC-90\2005
Lognormal-2P
MLE SRM MED FM
F=111/S=0


Pdf Line
GPC-90\2006
Lognormal-2P


Cumulative probability for the truncated 
data(90%) sampled in 1997-2006(GPC)


Probability density function for the truncated 
data(90%) sampled in 1997-2006(GPC)







Statistics analysis of gas ratio R1Statistics analysis of gas ratio R1
ReliaSoft Weibull++ 7 - www.ReliaSoft.com


Probability Density Function


Time, (t)


f(
t)


0.000 2.0000.400 0.800 1.200 1.600
0.000


6.000


1.200


2.400


3.600


4.800


Pdf


HSB-70\2003
Lognormal-2P
MLE SRM MED FM
F=11/S=0


Pdf Line


HSB-70\2005
Lognormal-2P
MLE SRM MED FM
F=13/S=0


Pdf Line


 
 
3/7/2007
3:28:38 PM


Cumulative probability for the truncated 
data(80%) sampled in 2003 and 2005(HSB)


Probability density function for the truncated 
data(80%) sampled in 2003 and 2006(HSB)


ReliaSoft Weibull++ 7 - www.ReliaSoft.com
Probability - Lognormal


Time, (t)


U
nr


el
ia


bi
lit


y,
 F


(t
)


0.100 10.0001.000
1.000


5.000


10.000


50.000


99.000 Probability-Lognormal


HSB-70\2003
Lognormal-2P
MLE SRM MED FM
F=11/S=0


Data Points
Probability Line


HSB-70\2005
Lognormal-2P
MLE SRM MED FM
F=13/S=0


Data Points
Probability Line


 
 
3/7/2007
3:30:44 PM







Statistics analysis of gas ratio R1Statistics analysis of gas ratio R1
The distribution model fitting of the aggregated truncated data from Alliant, GPC and 
HSB ---lognormal distribution


Probability - Lognormal


Time, (t)


U
nr


el
ia


bi
lit


y,
 F


(t
)


0.010 10.0000.100 1.000
0.100


0.500


1.000


5.000


10.000


50.000


99.990


0.100


Probability-Lognormal


Data 1
Lognormal-2P
RRX SRM MED FM
F=1222/S=0


Data Points
Probability Line


 
 
3/6/2007
1:54:45 PM






_1236742896.pdf


A Revised Framework for the 
Transformer DGA Guide


Jim Dukarm


for WG C57.104
Spring 2007







Presentation Topics
Purpose and scope of the Guide
Main departures from earlier versions
Definition of transformer DGA
Components of DGA
DGA risk classification
Triage and review
DGA contexts
Review example







Purpose & Scope


Scope
− In-service transformers filled with mineral oil


Purpose
− Provide a practical and up-to-date approach to 


transformer DGA for persons who need it


Keep the main content simple and straightforward; put 
technicalities in appendices.







Main departures . . .


More of a tutorial style
More examples
Basic principles
Emphasis on detecting & interpreting suspicious 
change
Avoidance of “sacred numbers” where possible
Visual approach to diagnosis







Definition of Transformer DGA


Transformer dissolved-gas analysis (DGA) is the 
measurement and interpretation of gases dissolved in 
the insulating fluid of a transformer.







Components of DGA


Measurement-related
− Sampling, sample handling, gas analysis


(referred to other documents)
− Data quality checking
− Handling measurement uncertainty


Interpretation
− Triage & risk classification
− Fault detection
− Diagnosis







DGA risk classification


Low to normal risk


Higher than normal risk


Very high risk


Immediate failure 
expected


(Gray circle represents units 
which will actually fail)


Risk = Failure cost  x  Probability of failure within 
next screening interval







Triage & Review


Triage
− Initial separation of “sheep” from “goats”
− Based on presence or absence of suspicious change


(increments or trends) or possible data quality 
problems


− “Sheep” considered OK (risk classification 1)
− “Goats” subjected to review


Review
− Based largely on examination of graphical evidence
− Risk class, resampling, diagnosis, action







DGA contexts


DGA context is based on sampling interval, and each 
has its particular concerns.
Initial sample
Periodic screening (long interval)
Surveillance (short interval)
Monitoring (several samples per day)







Review example
Gas Analysis


Sample date 2006-08-06 2005-09-11 2004-03-13
Fluid temp C 30 30 30
Hydrogen (H2) 20 0 0
Methane (CH4) 153 25 6
Ethane (C2H6) 476 39 0
Ethylene (C2H4) 146 5 0
Acetylene (C2H2) 0 0 0
Carbon Monoxide (CO) 253 273 95
Carbon Dioxide (CO2) 5482 4555 4783
Oxygen (O2) 3558 4189 12989
Nitrogen (N2) 21180 78569 90001
Total heat gas 775 69 6
TDCG 1048 342 101
O2/N2 0.17 0.05 0.14
Reference days 329 547 0
Risk class ? 2 1
Diagnosis ? T1 -
Retest days ? 365 365
Retest date ? 1998-09-11 1997-03-13


The 2004 sample had very little combustible gas. In 2005 there were discernible increases in all 3 heat gases, 
suggesting T1 and risk class 2. Decision was made to continue with screening. By 2006 heat gases had 
increased significantly.







Review example - continued


H2 CH4 C2H6 C2H4 C2H2 CO


0


50


100


150


200


250


300


350


400


450


500


Combus tible  Ga s e s  (2006-08-06)


pp
m







Review example - continued
In the latest sample we see parallel significant 
increases in H2 and the heat gases since the previous 
screening sample. No apparent involvement of COx.
Both the triangle and the combustible gases bar chart 
indicate a mid-range thermal fault (T2).
Classify as a “3” and recommend weekly 
surveillance sampling and other testing (e.g. I.R.) 
until decision can be made.







Review example - continued
Gas Analysis


Sample date 2006-08-06 2005-09-11 2004-03-13
Fluid temp C 30 30 30
Hydrogen (H2) 20 0 0
Methane (CH4) 153 25 6
Ethane (C2H6) 476 39 0
Ethylene (C2H4) 146 5 0
Acetylene (C2H2) 0 0 0
Carbon Monoxide (CO) 253 273 95
Carbon Dioxide (CO2) 5482 4555 4783
Oxygen (O2) 3558 4189 12989
Nitrogen (N2) 21180 78569 90001
Total heat gas 775 69 6
TDCG 1048 342 101
O2/N2 0.17 0.05 0.14
Reference days 329 547 0
Risk class 3 2 1
Diagnosis T2 T1 -
Retest days 7 365 365
Retest date 2006-08-13 1998-09-11 1997-03-13


DGA surveillance and other testing are ordered to support an investigation as to what may be happening 
and whether repairs may be required.







Technical appendices (partial list)


DGA calculations
− Ratios and increments, taking into account measurement uncertainty


− Linear regression for data with uncertainty (average rate of change, trend line)


DGA charts
− History line charts for gas concentrations & load


− Stacked area chart (combustible gases)


− Bar charts for combustible gas concentrations


− Log-log scatter plots for gas ratios


− Duval triangle for diagnosis & fault evolution


Lots of case histories
− Fault examples


− Normal operation, stray gassing, bad data






_1235372896.pdf


C57.139 


Dissolved Gas Analysis 
Of Load Tap Changers


Working Group


C57.139 


Dissolved Gas Analysis 
Of Load Tap Changers


Working Group


Data Analysis Update – Spring 2007







Data Analysis AgendaData Analysis Agenda


1. Update of activity1. Update of activity


2. Data analysis2. Data analysis


3. Review examples in reverse3. Review examples in reverse


4. Discuss conclusions4. Discuss conclusions







Activity UpdateActivity Update


• More data has been received
• Past concerns to identify “bad actors” using 


ratios and limits were discussed at the Fall 
meeting.


• Subcommittee formed to work further on data 
analysis (David Wallach, Jim Dukarm, and 
Shuzhen Xu) to discuss alternative methods to 
look at data statistically


• Subcommittee held multiple conference calls 
with support of WebEx & MS Live Meeting







Activity UpdateActivity Update


• Last meeting - we discussed working the 
process in reverse using LTC’s with known 
contact problems.  Two examples have 
been worked.







Data AnalysisData Analysis


• Minutes from Fall 2006







Data AnalysisData Analysis
• Planning call on January 4, 2007


– Use of 90th percentile results will depend on amount of data for a 
given model.


– LTC gasses are far from a normal distribution.  Most results are
low so elementary methods may not apply.


– We have not performed any advanced curve fitting techniques to 
date.


– Maybe have a “don’t care” limit and above which you can 
analyze.  Ratios give you relative rates of generation.


– Path forward from January 4th meeting –
• Dave provide data in Excel, model lookup table, and the latest 


version of the proposed LTC guide type table to Jim and Shuzhen to 
plot some statistical charts.  Results will be exchanged.  Jim will 
check with some customers to enlarge the database for the 
committee work.


• We can also have and look at 90th and 95th percentiles by model or 
type.







Update from Jim DukarmUpdate from Jim Dukarm


• Programmatic approach…
– A spreadsheet is fine for quick exploratory 


data analysis, but is not suitable for doing a 
more extensive analysis in a repeatable way.


– There are some kinds of statistical 
investigation that spreadsheets don't support.


– Some software was written to provide fast, 
repeatable data analysis and graphing.


– As new questions arise, it is not difficult to 
create new report-generating scripts to 
address those questions.







Update from Jim DukarmUpdate from Jim Dukarm


• Programmatic approach…
– Question 1: Do the distributions of gas 


concentrations and gas ratios differ year by 
year, and does lumping all measurements 
together change the distribution?


– Answer: Apparently the distributions of 
concentrations and ratios are very similar year 
to year and also when all years are lumped 
together.


Note: these distributions are for one company at a time -
data from different companies was not mixed.







Update from Jim DukarmUpdate from Jim Dukarm


Two-Sample Kolmogorov-Smirnov Test
(Values near zero indicate distinct distributions)
Variable: ETHYLENE (C2H4) - DUKE LTC's - Type AS1X


Year 1994 1995 1996 1997 1998 1999
1995 0.3364 -- -- -- -- --
1996 0.5911 0.6776 -- -- -- --
1997 0.4090 0.4512 0.3151 -- -- --
1998 0.7658 0.4756 0.9148 0.6315 -- --
1999 0.6465 0.2843 0.4316 0.5058 0.6220 --
ALL 0.4961 0.4527 0.6455 0.1629 0.8142 0.7639


Conclusion:  Year-to-year and lumped distributions do not differ.







Update from Jim DukarmUpdate from Jim Dukarm


Two-Sample Kolmogorov-Smirnov Test
(Values near zero indicate distinct distributions)
Variable: C2H4/C2H2 - DUKE LTC's - Type AS1X


Year 1994 1995 1996 1997 1998 1999
1995 0.7848 -- -- -- -- --
1996 0.0218 0.0906 -- -- -- --
1997 0.0143 0.0604 0.9706 -- -- --
1998 0.0255 0.0996 0.3149 0.3071 -- --
1999 0.0629 0.3576 0.9539 0.7890 0.1796 --
ALL 0.0119 0.0758 0.8275 0.6539 0.0642 0.4886


Conclusion:  Year-to-year and lumped distributions do not differ.







Update from Jim DukarmUpdate from Jim Dukarm


• Programmatic approach…
– Question 2: Does the ethylene/acetylene ratio 


behave similarly in all non-vacuum LTC's? Or 
within LTC types?


– Answer: Generally not!







Update from Jim DukarmUpdate from Jim Dukarm


Two-Sample Kolmogorov-Smirnov Test
(Values near zero indicate distinct distributions)
Variable: C2H4/C2H2 - DUKE LTC's


Type AS1X AS2X ATS1R
AS2X 0.0312 -- --
ATS1R 0.0001 0.0000 --
ATS1X 0.0000 0.0000 0.0000


Conclusion:  Multi-year distributions of C2H4/C2H2 differ between 
most LTC types at this company.


In fact, these distributions also mostly differed even for the same 
LTC type between companies.







Update from Jim DukarmUpdate from Jim Dukarm


Conclusion:  Duke AS2X and AS1X have similar C2H4/C2H2 distributions.







Update from Jim DukarmUpdate from Jim Dukarm


Conclusion:  Duke ATS1R and AS1X have different C2H4/C2H2 distributions.







Update from Jim DukarmUpdate from Jim Dukarm


Conclusion:  Duke ATS1R and AS2X have different C2H4/C2H2 distributions.







Update from Jim DukarmUpdate from Jim Dukarm


• Tentative Conclusions
– This analysis has not been carried out for other gas ratios, but it 


is expected that the results will be similar.
– Although some rough similarities in C2H4/C2H2 distributions do 


appear, a purely statistical approach to ratio-based LTC 
diagnosis seems unpromising.


– Common practice in the industry (and recent work by Duval) 
indicate that it should be possible to establish workable 
diagnostic limits for ratios based on study of DGA data for LTC's 
whose contact condition has been determined by inspection.


– Detailed results of statistical analysis will be made available to 
the WG as zipped collections of html files (web pages).







Update from Shuzhen XuUpdate from Shuzhen Xu
• The statistic analysis was only conducted on the 


data from Model AS1X (Arcing Switch in Oil, 
Single Compartment, Reactance type) and will be 
continued in the future. 


• Observations from data analysis
– The gas concentrations and ratios don’t follow normal 


distribution.
– The phenomenon of heterogeneousness was found in 


some gas concentrations and ratios distributions.
– Differentiating the data of the “healthy” units from those 


of problematic units is necessary before conducting 
meaningful statistic analysis. 


• The differentiation may be possible for the gas ratios  but may be 
impossible for gas concentrations due to the lack of operation counts?







Update from Shuzhen XuUpdate from Shuzhen Xu


• Example1 of data 
analysis.
– Data: the ratio between 


ethylene to acetylene 
R1=(C2H4/C2H4)


– Target model: AS1X
– Mixed-weibull model fits 


the data best
– Data are not from the 


same population 
statistically


Probability - Lognormal


Time, (t)


U
nr


el
ia
bi
lit
y,
 F
(t
)


0.010 1000.0000.100 1.000 10.000 100.000
0.100


0.500


1.000


5.000


10.000


50.000


99.990


0.100


Probability-Lognormal


Data 1
Lognormal-2P
RRX SRM MED FM
F=1019/S=0


Data Points
Probability Line


 
 
3/5/2007
3:24:23 PM


Probability - Weibull


Time, (t)


U
nr


el
ia
bi
lit
y,
 F
(t
)


0.100 1000.0001.000 10.000 100.000
0.010


0.050


0.100


0.500


1.000


5.000


10.000


50.000


90.000


99.990


0.010


Probability-Weibull


ratio-all
Weibull-Mixed
MLE SRM MED FM
F=1025/S=0


Data Points
Probability Line


 
 
3/5/2007
4:34:16 PM


Lognormal 
distribution 
fitting results


Mixed-weibull
distribution 
fitting results







Update from Shuzhen XuUpdate from Shuzhen Xu


• Example 2 of data 
analysis.
– Data: Ethylene
– Target model: AS1X
– Mixed-weibull model fits the 


data best
– Data are not from the same 


population statistically


2 parameter 
weibull
distribution 
fitting results


Mixed-weibull
distribution 
fitting results


ReliaSoft Weibull++ 7 - www.ReliaSoft.com


Probability - Weibull


β=0.4882, η=834.1233


Time, (t)


U
nr


el
ia
bi
lit
y,
 F
(t
)


1.000 1000000.00010.000 100.000 1000.000 10000.000 100000.000
0.010


0.050


0.100


0.500


1.000


5.000


10.000


50.000


90.000


99.990


0.010


Probability-Weibull


Data 1
Weibull-2P
MLE SRM MED FM
F=1025/S=0


Data Points
Probability Line


 
 
3/5/2007
4:31:19 PM


ReliaSoft Weibull++ 7 - www.ReliaSoft.com


Probability - Weibull


β[1]=1.5585, η[1]=12.0931, Ρ[1]=0.1419; β[2]=1.1432, η[2]=73.6933, Ρ[2]=0.1410; β[3]=0.6509, η[3]=1753.9480, Ρ[3]=0.7171


Time, (t)


U
nr


el
ia
bi
lit
y,
 F
(t
)


1.000 1000000.00010.000 100.000 1000.000 10000.000 100000.000
0.010


0.050


0.100


0.500


1.000


5.000


10.000


50.000


90.000


99.990


0.010


Probability-Weibull


Data 1
Weibull-Mixed
MLE SRM MED FM
F=1025/S=0


Data Points
Probability Line


 
 
3/5/2007
4:32:05 PM







Review in reverse – Example #1Review in reverse – Example #1
• October 26, 2006:  Duke Energy southern region had potential problems associated 


with Bank 3 at XXXXXXX Retail (C04901515). After looking at a few other predictors 
it was obvious we had issues inside the LTC compartment. Internal inspection was 
performed. Attached you’ll see photos of these findings. (z & x phases the worst)  


• A little history
– Maximo records indicated that the last internal inspection of the contacts was performed in 


1999. The last external inspection/filter change was on March 8, 2006.   DGA and filter 
condition results at that time didn’t point to signs of trouble.


– Between March 8, 2006 and October 25, 2006 the LTC has operated around 3458 
operations and the filter pressure was noted at 45-50 psi. on October 25, 2006. Actual start 
up pressure during the last external inspection with filter change was 13 psi. on March 8, 
2006.


– Working with Voltage Quality the field installed recorders on each phase for monitoring and 
operated the LTC a couple of times in the lower and raise positions.  Field personnel did 
notice a change in tone from the 9L to the 10L position (not a good sign). The results from 
the recordings were distorted voltage and current wave forms.


– The LTC was locked down on a tap that was a happy medium and cleared on October 25, 
2006. This unit typically stays on the lower or buck side of neutral so it was apparent these 
contacts would be in the worst condition. After opening the compartment this outside-in 
assessment was true.


– We replaced all moving and stationary contacts, replacing all gaskets, replacing oil, ratio, 
dielectric, and then re-charge for load. 







FilterFilter







Z phase contactsZ phase contacts







Y phase contactsY phase contacts







X phase contactsX phase contacts







Serial Number C04901515 DataSerial Number C04901515 Data


R1 R2 R3 R4 R5 R6 Hot Metal Sum
0.666667 0.666667 1.333333 1.333333 0 0 2
0.045147 0.606061 0.06772 0.909091 0 0 3
0.066667 0.222222 0.133333 0.444444 1 2 4
0.408163 0.408163 1.020408 1.020408 0 0 5


0.1 0.6 0.166667 1 0 0 5
0.070423 0.454545 0.15493 1 0.5 2.5 11
0.108108 0.444444 0.162162 0.666667 0.333333 8 12


4.2 4.2 5.9 5.9 1.428571 4.2 59


SAMPLEDATE H2 CH4 C2H6 C2H4 C2H2 CO TOTALGAS CO2 REASON
4/2/2004 0:00 0 1 0 1 1.5 24 8.8 303 ROUTINE
5/9/2005 0:00 41 1 0 2 3.3 204 6.1 613 ROUTINE


1/12/2000 0:00 21 1 1 2 9 37 7.6 507 ROUTINE
1/13/2003 0:00 0 3 0 2 4.9 49 6.8 582 ROUTINE
5/2/1999 0:00 25 2 0 3 5 97 10.6 714 ROUTINE


8/16/2001 0:00 60 4 2 5 11 213 8.6 1333 ROUTINE
7/17/2002 0:00 56 3 1 8 18 252 8.2 47 ROUTINE
3/8/2006 0:00 0 7 10 42 10 121 7.7 903 ROUTINE







Example #1 - RatiosExample #1 - Ratios


McGraw 550CS LTC, Sealed with continuous online filtration


Number of records 561


Average Values, Ratios
R1 R2 R3 R4 R5 R6


0.365 0.788 0.807 2.961 0.592 4.391


Standard Deviation, Ratios less than 90th percentile
R1 R2 R3 R4 R5 R6


0.097 0.132 0.203 0.389 0.341 4.050


Percentiles, Ratios
Percentile R1 R2 R3 R4 R5 R6


10.00% 0.043 0.160 0.088 0.233 0.000 0.000
20.00% 0.098 0.211 0.176 0.296 0.000 0.000
30.00% 0.127 0.235 0.222 0.337 0.146 0.143
40.00% 0.152 0.253 0.249 0.387 0.250 0.905
50.00% 0.180 0.286 0.283 0.450 0.375 2.500
60.00% 0.207 0.323 0.345 0.537 0.500 4.167
70.00% 0.244 0.373 0.438 0.667 0.600 7.000
80.00% 0.297 0.474 0.597 1.011 0.878 9.750
90.00% 0.429 0.769 1.330 2.714 1.286 11.885
95.00% 0.690 1.786 2.759 8.064 2.000 13.541
98.00% 1.898 4.366 8.529 21.289 3.089 15.629







Example #1 ConclusionsExample #1 Conclusions


• Ratios could have triggered concerns after 
the “damage was done”


• Duke Energy’s traditional approach would 
NOT have caught this
– Sum of hot metals
– Hot metal ppm trend







Example #2Example #2
• XXXXXX Retail is a one bank station.  This transformer (Serial Number C04901512) 


still had the old balance beam control.  A service tech was investigating a low voltage 
complaint when he discovered that the LTC would not operate.  Field personnel went 
there and noticed the LTC would attempt to raise but would only go about half way 
and then return to the previous step.  After a few times of this happening, we decided 
to lock it down and install a portable transformer to clear the bank and go into the 
mechanism.


• The reason the LTC wouldn’t operate is because one set of moving contacts had 
welded itself to one of the stationary.  This transformer had an internal PM in 2003 
and the low resistance contacts were installed at this time.


• This transformer had operated 31,133 times since January of this year in 2006 
(3459/month).  In 2005, it operated 31,907 times (2658/month) and was pretty much 
normal in 2004 operating 8157 times (680/month).  Field personnel are convinced 
that the number of operations was due to the balance beam control.  A new Beckwith 
2001 two days later showed 14 operations a day.  Much better!  Filter was pretty 
much black.  DGA was off of the charts.


• When the contacts were replaced and we operated the mechanism, we noticed that 
the motor seemed to strain when it went from neutral to raise 1. This is when the 
reversing switch operates also.  We replaced the motor and gear box and then it 
sounded OK.  I don’t know if the motor got weak when the contacts welded and the 
motor stalled or because of the number of operations.  Anyway, we pretty much have 
a new tap changer mechanism and control now.







Second example photosSecond example photos







Second example photosSecond example photos


OLDNEW







Serial Number C04901512 DataSerial Number C04901512 Data


EQUIPNUM SAMPLEDATE H2 CH4 C2H6 C2H4 C2H2 CO TOTALGAS CO2 REASON
C04901512 4/23/1998 0:00 0 0 0 1 0 32 10.6 320 AFTER DEGAS
C04901512 6/3/1998 0:00 27 0 0 8 41 77 4 439 NEW FLUID
C04901512 8/27/1996 0:00 83 7 5 25 113 133 9.9 1852 ROUTINE
C04901512 4/6/1998 0:00 28 14 4 40 218 113 8.9 1234 BEFORE DEGAS
C04901512 10/1/1998 0:00 23 16 7 84 403 10 9.3 508 ROUTINE
C04901512 6/5/1996 0:00 100 95 48 39 122 513 7.3 2870 ROUTINE
C04901512 9/3/2002 0:00 51 28 17 168 720 126 9.1 28 ROUTINE
C04901512 1/20/2003 0:00 85 62 10 145 750 28 9.7 494 ROUTINE
C04901512 5/5/1999 0:00 58 41 16 190 1031 16 11.4 511 ROUTINE
C04901512 1/6/2000 0:00 54 38 18 203 1052 3 9.4 510 ROUTINE
C04901512 1/15/2004 0:00 121 66 24 314 1400 27 7.7 391 ROUTINE
C04901512 1/17/2006 0:00 235 127 81 849 3500 15 9.1 319 ROUTINE
C04901512 11/14/2005 0:00 146 154 79 845 3300 29 8.7 524 ROUTINE


R1 R2 R3 R4 R5 R6 Hot Metal Sum
0 0 0 0 0 0 1


0.117647 0.195122 0.117647 0.195122 0 0 8
0.127551 0.221239 0.188776 0.327434 0.714286 5 37
0.162602 0.183486 0.235772 0.266055 0.285714 10 58
0.197183 0.208437 0.251174 0.265509 0.4375 12 107
0.175676 0.319672 0.81982 1.491803 0.505263 0.8125 182
0.217899 0.233333 0.276265 0.295833 0.607143 9.882353 213
0.173653 0.193333 0.25988 0.289333 0.16129 14.5 217
0.174472 0.184287 0.226814 0.239573 0.390244 11.875 247
0.183544 0.192966 0.234177 0.246198 0.473684 11.27778 259
0.206443 0.224286 0.265615 0.288571 0.363636 13.08333 404
0.227309 0.242571 0.282999 0.302 0.637795 10.48148 1057
0.245212 0.256061 0.312826 0.326667 0.512987 10.6962 1078







Specific Example - RatiosSpecific Example - Ratios


McGraw 550CS LTC, Sealed with continuous online filtration


Number of records 561


Average Values, Ratios
R1 R2 R3 R4 R5 R6


0.365 0.788 0.807 2.961 0.592 4.391


Standard Deviation, Ratios less than 90th percentile
R1 R2 R3 R4 R5 R6


0.097 0.132 0.203 0.389 0.341 4.050


Percentiles, Ratios
Percentile R1 R2 R3 R4 R5 R6


10.00% 0.043 0.160 0.088 0.233 0.000 0.000
20.00% 0.098 0.211 0.176 0.296 0.000 0.000
30.00% 0.127 0.235 0.222 0.337 0.146 0.143
40.00% 0.152 0.253 0.249 0.387 0.250 0.905
50.00% 0.180 0.286 0.283 0.450 0.375 2.500
60.00% 0.207 0.323 0.345 0.537 0.500 4.167
70.00% 0.244 0.373 0.438 0.667 0.600 7.000
80.00% 0.297 0.474 0.597 1.011 0.878 9.750
90.00% 0.429 0.769 1.330 2.714 1.286 11.885
95.00% 0.690 1.786 2.759 8.064 2.000 13.541
98.00% 1.898 4.366 8.529 21.289 3.089 15.629







Example #2 ConclusionsExample #2 Conclusions


• Ratio of C2H4/(C2H2+H2) appears to be 
sensitive but the other ratios would not have 
supported a concern.


• Duke Energy’s traditional approach would 
support the problems found however internal 
trigger levels were not met.
– Sum of hot metals
– Hot metal ppm trend


• The 90th percentile of this ratio would probably 
not raise a flag until the contacts were already in 
poor condition.







SummarySummary


• Preliminary statistical investigation was conducted by 
Shuzhen and Jim on four LTC DGA data sets - from 
Alliant, Duke, GBC, and HSB.


• Work was concentrated on ethylene (C2H4) and the 
ethylene-acetylene ratio (C2H4/C2H2)


• Shuzhen used some powerful statistical analysis 
software tools to investigate these particular cases, and 
Jim wrote statistical software which would be able to 
carry out analyses similar to Shuzhen's on a larger 
scale after we had figured out what seemed most 
fruitful.







SummarySummary
• We found that the distributions of ethylene and the 


ethylene/acetylene ratio were very messy and 
inconsistent from company to company and between 
arcing LTC types.  It would not be useful to try basing 
diagnostic limits on percentiles of such distributions.


• By ignoring all the ratio values above a certain 
percentile (different for each distribution), it is possible 
to find a single (lognormal) distribution that apparently 
describes the ethylene/acetylene distribution for AS1X 
LTC's in good condition.  From this we may be able to 
derive a useful limit for distinguishing between mostly 
good LTC's and mostly deteriorating ones.


• We expect to be able to derive combustible gas 
concentration limits that will be useful for vacuum-type 
LTC's, but so far that work has not been started.


• We will now extend the scope of our analysis to all 
combustible gases, all ratios,and all LTC types to try to 
arrive at generally useful results.







SummarySummary
• It seems clear that it will be necessary to use gas ratio 


values for inspected arcing-type LTC's to confirm the 
usefulness of our statistically-derived ratio limit(s) and 
perhaps to develop some higher limits characterizing 
more advanced states of deterioration.


• Other than requiring ratio values to be calculated from 
gas concentrations at or above the respective detection 
limit (to avoid gross relative uncertainty), we do not 
expect gas concentration limits to be diagnostically 
useful for arcing-type LTC's.  This will be checked, 
however.


• Conversely, because of the low gas concentrations 
usually found in vacuum-type LTC's, we expect that gas 
concentration limits will be more diagnostically useful 
than gas ratios for vacuum-type LTC's.







Proposed Path Forward for GuideProposed Path Forward for Guide
Data 


Analysis 
performed 


to date


Check use of ratios but likely 
pursue statistical approach to 


screening with ppm
concentration values.


Pursue statistical approach for 
ratios by type using truncated 


data.


Vacuum Arcing


Prepare final LTC 
DGA Guide, Rev 0 


beginning after 
Minneapolis meeting






